## 2027
Site | Substation | Voltage (kV) | Longitude Easting (deg) | Latitude Northing (deg) | Hosting Capacity (MW)
[5 empty] | Load_0%_flex | Load_5%_flex | Load_10%_flex | Load_20%_flex | Prod_0%_flex | Prod_5%_flex | Prod_10%_flex | Prod_20%_flex | PV_0%_flex | PV_5%_flex | PV_10%_flex | PV_20%_flex | Wind_0%_flex | Wind_5%_flex | Wind_10%_flex | Wind_20%_flex | Battery_0%_flex | Battery_5%_flex | Battery_10%_flex | Battery_20%_flex
AALST | AALST 70 | 70 | 4.0504 | 50.9313 | 1.8 | 15 | 21.3 | 30.9 | 6.5 | 32.8 | 43.4 | 50 | 29.8 | 50 | 50 | 50 | 16.2 | 39.3 | 50 | 50 | 1.7 | 2 | 2.2 | 2.6
AALTR | AALTR 36 | 36 | 3.4527 | 51.1018 | 11.4 | 16.5 | 24 | 41.7 | 8.2 | 60 | 60 | 60 | 13.2 | 60 | 60 | 60 | 37.3 | 60 | 60 | 60 | 7.3 | 19.6 | 26.9 | 38.8
AARSC | AARSC 70 | 70 | 4.841 | 50.986 | 1.4 | 2.4 | 5.4 | 16.1 | 1.8 | 50 | 50 | 50 | 2.8 | 50 | 50 | 50 | 6.9 | 50 | 50 | 50 | 1.4 | 2.4 | 5.2 | 14.1
ABEE | ABEE 70 | 70 | 5.3713 | 50.4943 | 0.7 | 2.2 | 6.3 | 35 | 0.7 | 18 | 33.7 | 50 | 1.2 | 50 | 50 | 50 | 1 | 22.1 | 32.5 | 50 | 0.7 | 1.6 | 2.4 | 14.3
ACHEN | ACHEN 70 | 70 | 5.0554 | 50.2605 | 2.3 | 5.8 | 9 | 43.8 | 1.9 | 4.4 | 5.5 | 9.8 | 5.7 | 42.6 | 60 | 60 | 2.3 | 4.5 | 5.9 | 10.1 | 1.9 | 4.4 | 5.5 | 9.8
ACHEN | ACHEN380 | 380 | 5.0554 | 50.2605 | 52.6 | 300 | 300 | 300 | 68.2 | 162.6 | 272.6 | 300 | 157 | 300 | 300 | 300 | 142.9 | 300 | 300 | 300 | 52.6 | 162.6 | 272.6 | 300
AIRLI | AIRLI 30 | 30 | 3.8557 | 50.4778 | 1.3 | 4.6 | 10.9 | 15 | 8 | 20 | 20 | 20 | 10.3 | 19.4 | 20 | 20 | 17.6 | 20 | 20 | 20 | 1.1 | 4.2 | 9.6 | 13.2
ALKEN | ALKEN 70 | 70 | 5.2922 | 50.8753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ALLEU | ALLEU 70 | 70 | 5.5264 | 50.6751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AMEL | AMEL 70 | 70 | 6.1795 | 50.3619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AMERC | AMERC150 | 150 | 4.3946 | 50.4314 | 12.8 | 22.7 | 28.9 | 49.1 | 18.1 | 92.2 | 131.4 | 175 | 32.3 | 175 | 175 | 175 | 35.2 | 95 | 175 | 175 | 12.8 | 21 | 25.2 | 35.8
AMPSI | AMPSI 70 | 70 | 5.2982 | 50.5342 | 1.5 | 3.6 | 14.6 | 35.1 | 1.2 | 25.5 | 43.3 | 50 | 2 | 50 | 50 | 50 | 1.6 | 36.9 | 50 | 50 | 1.2 | 2.2 | 3.3 | 18.6
ANDUM | ANDUM150 | 150 | 5.4857 | 50.9403 | 9.3 | 31.8 | 49.7 | 172 | 14.2 | 175 | 175 | 175 | 43.2 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 9.2 | 26.4 | 40.8 | 110.1
ANGLE | ANGLE 70 | 70 | 5.582 | 50.6184 | 10.3 | 29.6 | 39.7 | 50 | 1.6 | 16.8 | 35.5 | 50 | 2.6 | 50 | 50 | 50 | 21.3 | 50 | 50 | 50 | 1.6 | 16.8 | 25 | 34.3
ANS | ANS 150 | 150 | 5.5233 | 50.655 | 4.2 | 27.1 | 38 | 71.5 | 4.4 | 21.8 | 67.2 | 175 | 22.3 | 43 | 63.2 | 175 | 11.6 | 98.2 | 161.2 | 175 | 4.2 | 20 | 27.9 | 39.8
ANS | ANS 70 | 70 | 5.5233 | 50.655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ANTHI | ANTHI 70 | 70 | 5.5301 | 50.4727 | 0.7 | 1.4 | 3 | 31.5 | 0.7 | 5.7 | 11.6 | 42.6 | 1.2 | 50 | 50 | 50 | 1 | 30.4 | 50 | 50 | 0.7 | 1.3 | 2.9 | 27.3
ANTOI | ANTOI150 | 150 | 3.4428 | 50.5716 | 1.6 | 17.6 | 33 | 62.8 | 15.2 | 58.6 | 171.6 | 175 | 32.7 | 175 | 175 | 175 | 19.9 | 88.6 | 175 | 175 | 1.6 | 11.9 | 24.4 | 54.4
ARLON | ARLON 70 | 70 | 5.8178 | 49.6711 | 1 | 1.6 | 2.2 | 4.4 | 1.2 | 2.3 | 3.4 | 13.4 | 2.2 | 4.2 | 5.1 | 8.1 | 1.7 | 5.4 | 9.9 | 50 | 1 | 1.6 | 2.2 | 4.4
AUBAN | AUBAN 70 | 70 | 5.7943 | 49.5668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUBAN | AUBAN220 | 220 | 5.7943 | 49.5668 | 18.4 | 31.5 | 47.2 | 89.2 | 23.1 | 51 | 83.7 | 175 | 29.7 | 97.4 | 159.2 | 175 | 37.2 | 100.7 | 175 | 175 | 18.4 | 31.4 | 44.7 | 84.9
AUBAN | AUBAN380 | 380 | 5.7943 | 49.5668 | 21.1 | 32.2 | 42.5 | 80.9 | 5.7 | 37.8 | 82 | 163.1 | 15 | 100.5 | 190.5 | 300 | 8.4 | 110.3 | 182.3 | 300 | 5.7 | 32.1 | 42.5 | 80.8
AUVEL | AUVEL 30 | 30 | 4.6212 | 50.4556 | 0.6 | 1.1 | 3 | 13.5 | 7 | 21.1 | 60 | 60 | 60 | 60 | 60 | 60 | 13.5 | 60 | 60 | 60 | 0.6 | 1.1 | 3 | 13.5
AUVEL | AUVEL 70 | 70 | 4.6212 | 50.4556 | 1.4 | 2.7 | 11.5 | 31.8 | 0.6 | 0.9 | 1.5 | 12.7 | 1 | 10.8 | 21.6 | 50 | 0.6 | 0.9 | 1.1 | 1.7 | 0.6 | 0.9 | 1.5 | 12.1
AVERN | AVERN150 | 150 | 5.0602 | 50.7132 | 3.5 | 38.8 | 54.2 | 107.5 | 3 | 23.8 | 55.3 | 140.5 | 5.6 | 123.6 | 175 | 175 | 3.7 | 6.6 | 12.5 | 62.1 | 3 | 20.1 | 38.1 | 54.9
AVLGM | AVLGM380 | 380 | 3.469 | 50.7824 | 87 | 300 | 300 | 300 | 91.1 | 251.8 | 300 | 300 | 268.6 | 300 | 300 | 300 | 103.7 | 237.5 | 300 | 300 | 87 | 231.7 | 300 | 300
AWIRS | AWIRS 70 | 70 | 5.4151 | 50.5846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AWIRS | AWIRS150 | 150 | 5.4151 | 50.5846 | 5.2 | 18.8 | 33.5 | 77.1 | 13 | 34.6 | 58.8 | 175 | 42.9 | 175 | 175 | 175 | 20.6 | 157.9 | 175 | 175 | 5.2 | 15.9 | 28.5 | 42.8
AWIRS | AWIRS220 | 220 | 5.4151 | 50.5846 | 9.3 | 31.5 | 44.1 | 90.4 | 15.2 | 32.8 | 59.1 | 175 | 28.4 | 175 | 175 | 175 | 28.3 | 175 | 175 | 175 | 12.9 | 23.5 | 27.4 | 38.2
BAASR | BAASR 70 | 70 | 4.1799 | 51.028 | 1.9 | 20.9 | 30.5 | 50 | 8.2 | 39 | 50 | 50 | 27.9 | 50 | 50 | 50 | 20.6 | 50 | 50 | 50 | 1.6 | 2 | 2.2 | 2.7
BAISY | BAISY 36 | 36 | 4.488 | 50.6527 | 2.5 | 5 | 6.2 | 11.5 | 1.8 | 17 | 32.4 | 60 | 4.1 | 60 | 60 | 60 | 2.1 | 21.2 | 56.3 | 60 | 1.8 | 4.7 | 5.3 | 7.1
BAISY | BAISY150 | 150 | 4.488 | 50.6527 | 3.7 | 5 | 6.2 | 11.5 | 4.8 | 15.1 | 22.5 | 61.2 | 7.5 | 26.1 | 31.6 | 50.5 | 5.6 | 12.8 | 28.6 | 121.6 | 3.5 | 4.7 | 5.3 | 7.1
BALEN | BALEN150 | 150 | 5.2222 | 51.2019 | 6.6 | 13.7 | 31.9 | 149.3 | 12 | 175 | 175 | 175 | 29.6 | 135.1 | 175 | 175 | 17.5 | 175 | 175 | 175 | 5.4 | 13.5 | 31.6 | 98.5
BASSW | BASSW 36 | 36 | 4.6284 | 50.7232 | 1.1 | 4.9 | 5.8 | 8.9 | 4.8 | 15.1 | 20 | 20 | 7.5 | 20 | 20 | 20 | 5.6 | 12.9 | 20 | 20 | 1.1 | 4.6 | 5.3 | 7.5
BAUDO | BAUDO 70 | 70 | 3.8261 | 50.4704 | 1.5 | 7.3 | 8.5 | 10.6 | 1.5 | 7.5 | 8.9 | 11.2 | 2.5 | 24 | 30.9 | 43.2 | 2.1 | 8.7 | 11.3 | 18 | 1.5 | 5.7 | 6.9 | 8.9
BAUDO | BAUDO150 | 150 | 3.8261 | 50.4704 | 5.5 | 22.2 | 38.8 | 60.7 | 6.8 | 20.3 | 33.3 | 44.1 | 10.2 | 19.2 | 26.7 | 71.7 | 17.1 | 36.5 | 60.6 | 88 | 5.5 | 16.5 | 25.6 | 34.6
BEAGA | BEAGA150 | 150 | 4.2973 | 50.862 | 11.6 | 23.9 | 38.3 | 107.9 | 12.9 | 35.5 | 80.8 | 175 | 17 | 39.9 | 89.5 | 175 | 17.9 | 103 | 175 | 175 | 3.3 | 20.8 | 32 | 79.2
BEERN | BEERN 36 | 36 | 3.2976 | 51.1275 | 0.2 | 4.8 | 10.4 | 13.7 | 0 | 4.3 | 15.3 | 20 | 0 | 0 | 0.6 | 4.6 | 0.4 | 20 | 20 | 20 | 0 | 0.3 | 0.6 | 2.9
BEERS | BEERS 70 | 70 | 4.8533 | 51.3263 | 1.3 | 8.2 | 49 | 60 | 1.3 | 5.4 | 10 | 31.9 | 2 | 8 | 10.7 | 22.5 | 2.3 | 15.7 | 22.2 | 54.5 | 1.3 | 3.7 | 10 | 31.9
BEERS | BEERS150 | 150 | 4.8533 | 51.3263 | 4.1 | 29.4 | 86.4 | 175 | 3.9 | 8.6 | 16.4 | 40.6 | 6.8 | 14.2 | 17.9 | 31.4 | 5.3 | 15.8 | 28.5 | 86.7 | 3.9 | 8.6 | 16.4 | 40.6
BEREN | BEREN 36 | 36 | 4.2839 | 51.3399 | 0.2 | 0.4 | 0.5 | 0.5 | 7.7 | 13.5 | 14.8 | 18.4 | 13.9 | 20 | 20 | 20 | 8.3 | 18.3 | 20 | 20 | 0.2 | 0.4 | 0.4 | 0.4
BERIN | BERIN 70 | 70 | 5.2134 | 51.0668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BERIN | BERIN150 | 150 | 5.2134 | 51.0668 | 10.1 | 19.1 | 24.2 | 50.3 | 16.6 | 175 | 175 | 175 | 103.5 | 175 | 175 | 175 | 22.1 | 175 | 175 | 175 | 9.7 | 18.8 | 23.5 | 43.1
BERNE | BERNE220 | 220 | 5.7372 | 50.7535 | 8.4 | 16.1 | 26 | 60.9 | 7.2 | 19.6 | 38.2 | 175 | 18.8 | 105.3 | 175 | 175 | 14.6 | 126.8 | 175 | 175 | 7 | 14.9 | 18.8 | 30.8
BEVER | BEVER 70 | 70 | 6.0387 | 50.439 | 1 | 1.5 | 2.5 | 16.6 | 0.6 | 0.9 | 1.5 | 3.3 | 0.9 | 2.8 | 4 | 9.1 | 0.6 | 0.9 | 1.1 | 1.7 | 0.6 | 0.9 | 1.5 | 3.3
BEVER | BEVER110 | 110 | 6.0387 | 50.439 | 5.8 | 36.7 | 50.2 | 61.3 | 1.2 | 2.3 | 3.5 | 21.5 | 2.1 | 26.4 | 45.8 | 93.1 | 1.3 | 2 | 2.7 | 4.6 | 1.2 | 2.3 | 3.5 | 21.5
BIERG | BIERG 36 | 36 | 4.5973 | 50.7056 | 0.7 | 4.7 | 5.6 | 8.8 | 4.8 | 15.1 | 20 | 20 | 7.5 | 20 | 20 | 20 | 5.6 | 12.9 | 20 | 20 | 0.7 | 4.5 | 5.2 | 7.3
BILZE | BILZE 70 | 70 | 5.5055 | 50.8765 | 1.2 | 13.1 | 43.3 | 50 | 6.9 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 7.4 | 50 | 50 | 50 | 1.2 | 9.4 | 37.7 | 50
BLTOR | BLTOR150 | 150 | 3.1927 | 51.2614 | 6.5 | 22.4 | 41.3 | 85.4 | 6.7 | 115.6 | 175 | 175 | 10.8 | 175 | 175 | 175 | 18.3 | 175 | 175 | 175 | 4.1 | 20.3 | 30.8 | 66.2
BOISD | BOISD 70 | 70 | 4.8087 | 50.3823 | 1.4 | 2.8 | 5 | 21.6 | 0.7 | 1.1 | 1.5 | 12.1 | 1.5 | 18 | 35.1 | 50 | 0.8 | 1.2 | 1.5 | 2.2 | 0.7 | 1.1 | 1.5 | 12.1
BOMAL | BOMAL 70 | 70 | 5.5145 | 50.3771 | 0.6 | 1.9 | 6.4 | 24.8 | 0.8 | 16.1 | 24 | 45.5 | 2.2 | 50 | 50 | 50 | 1.8 | 20.3 | 50 | 50 | 0.6 | 1.6 | 4.6 | 22.3
BONNE | BONNE 70 | 70 | 5.8271 | 49.7105 | 1.1 | 1.8 | 2.3 | 4.7 | 1.3 | 1.9 | 2.8 | 10.4 | 1.7 | 3.1 | 3.8 | 6.1 | 1.6 | 4.6 | 8.5 | 50 | 1.1 | 1.8 | 2.3 | 4.7
BORGL | BORGL 70 | 70 | 5.3377 | 50.7914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BORNM | BORNM 70 | 70 | 4.2676 | 51.0896 | 1.9 | 20.7 | 29.3 | 50 | 7.6 | 18.9 | 30.3 | 50 | 27.6 | 50 | 50 | 50 | 15.3 | 36 | 50 | 50 | 1.6 | 2 | 2.2 | 2.7
BOTAN | BOTAN 36 | 36 | 4.3635 | 50.8552 | 1.8 | 20 | 20 | 20 | 2.7 | 20 | 20 | 20 | 17 | 20 | 20 | 20 | 3.2 | 20 | 20 | 20 | 1.4 | 20 | 20 | 20
BOVEN | BOVEN 36 | 36 | 4.435 | 50.832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BRAIN | BRAIN150 | 150 | 4.367 | 50.6861 | 3.7 | 5.1 | 6.2 | 11.6 | 4.8 | 12.8 | 19.2 | 52.1 | 6.4 | 22.5 | 27.3 | 43.6 | 5.3 | 10.8 | 24.1 | 102.5 | 3.7 | 4.7 | 5.3 | 7.1
BRESS | BRESS150 | 150 | 5.6123 | 50.6486 | 16 | 27.4 | 36.2 | 73.8 | 6.1 | 16.2 | 46 | 175 | 9.1 | 20.9 | 45.8 | 166.7 | 24.3 | 175 | 175 | 175 | 3.9 | 16.2 | 23.2 | 29.8
BRUEG | BRUEG150 | 150 | 4.2317 | 50.881 | 11.6 | 25.3 | 38.6 | 123 | 13 | 34.7 | 79.1 | 300 | 17.1 | 41 | 99.7 | 236.5 | 18 | 142 | 300 | 300 | 11.6 | 17 | 20.5 | 30.1
BRUEG | BRUEG380 | 380 | 4.2317 | 50.881 | 48.2 | 108.4 | 151.8 | 222.1 | 128.5 | 300 | 300 | 300 | 269.9 | 300 | 300 | 300 | 147.4 | 300 | 300 | 300 | 45.7 | 98 | 129.2 | 199.1
BRUGG | BRUGG 36 | 36 | 3.1991 | 51.216 | 7.2 | 18.4 | 29.8 | 60 | 6.7 | 60 | 60 | 60 | 10.8 | 60 | 60 | 60 | 18.3 | 60 | 60 | 60 | 4.1 | 20.1 | 29.7 | 60
BRUGG | BRUGG150 | 150 | 3.1991 | 51.216 | 7.2 | 18.4 | 29.8 | 72.5 | 6.7 | 103 | 167.5 | 175 | 10.8 | 175 | 175 | 175 | 18.3 | 175 | 175 | 175 | 4.1 | 20.1 | 29.7 | 61.4
BRUME | BRUME220 | 220 | 5.843 | 50.3755 | 5.1 | 39.6 | 56.9 | 116.1 | 3 | 23.4 | 75 | 169.4 | 5 | 103.8 | 175 | 175 | 3.4 | 5.5 | 9.3 | 46.4 | 3 | 23.4 | 56.5 | 114.5
BRUME | BRUME380 | 380 | 5.843 | 50.3755 | 18.6 | 37.1 | 73.3 | 300 | 49 | 181.7 | 300 | 300 | 163 | 300 | 300 | 300 | 63.3 | 300 | 300 | 300 | 18.6 | 37 | 73.1 | 300
BRUNY | BRUNY 36 | 36 | 3.2412 | 51.2072 | 7.5 | 18.2 | 20 | 20 | 6.7 | 20 | 20 | 20 | 10.8 | 20 | 20 | 20 | 18.3 | 20 | 20 | 20 | 4.1 | 20 | 20 | 20
BRUST | BRUST 70 | 70 | 5.2213 | 50.8147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BRUZU | BRUZU 36 | 36 | 3.2224 | 51.1939 | 4.1 | 12.5 | 19 | 20 | 6.7 | 20 | 20 | 20 | 10.8 | 20 | 20 | 20 | 18.3 | 20 | 20 | 20 | 4.1 | 18 | 20 | 20
BUDA | BUDA 36 | 36 | 4.413 | 50.9064 | 4.7 | 10.7 | 11.9 | 14.4 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 4.7 | 6.4 | 8.5 | 13
BUIZI | BUIZI150 | 150 | 4.2577 | 50.749 | 4.2 | 8.2 | 11.4 | 21.2 | 4.9 | 21.2 | 69 | 175 | 16.8 | 39.3 | 99 | 175 | 6.7 | 70.4 | 175 | 175 | 4.2 | 7.7 | 9.7 | 12.9
BURCH | BURCH150 | 150 | 4.348 | 51.2103 | 4.4 | 5.6 | 6.6 | 9.9 | 9 | 29.2 | 91.7 | 175 | 21.8 | 88.1 | 175 | 175 | 15.3 | 47.4 | 98.5 | 175 | 3.9 | 5.3 | 5.8 | 7.3
BVREN | BVREN 70 | 70 | 3.1268 | 50.9656 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BVREN | BVREN150 | 150 | 3.1268 | 50.9656 | 6.3 | 38.6 | 103 | 172.7 | 11.3 | 49 | 95.3 | 175 | 29.4 | 175 | 175 | 175 | 14.8 | 44.5 | 91.2 | 141.3 | 4.5 | 21.8 | 63.3 | 100.9
BWTON | BWTON150 | 150 | 2.9421 | 50.7707 | 3.1 | 31.6 | 81.3 | 100.1 | 25.2 | 175 | 175 | 175 | 122.2 | 175 | 175 | 175 | 53.9 | 175 | 175 | 175 | 2.3 | 34.6 | 63.1 | 76.6
CENTE | CENTE 36 | 36 | 4.3472 | 50.8942 | 0.8 | 11.6 | 12.8 | 15.7 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0.7 | 11.3 | 12.2 | 14.5
CHAMP | CHAMP 70 | 70 | 4.9038 | 50.4887 | 2.5 | 5.9 | 14.5 | 56.5 | 2.5 | 7.6 | 11.8 | 28.4 | 4.2 | 47.6 | 60 | 60 | 3 | 6.3 | 9.9 | 60 | 2.5 | 5.6 | 11.1 | 28.4
CHAMP | CHAMP380 | 380 | 4.9038 | 50.4887 | 24.9 | 70.6 | 137 | 300 | 29.1 | 213.3 | 300 | 300 | 123.8 | 300 | 300 | 300 | 37.6 | 236.6 | 300 | 300 | 24.8 | 63.6 | 115.3 | 300
CHASS | CHASS 70 | 70 | 4.5223 | 50.5303 | 4.5 | 18.5 | 26.1 | 36.6 | 0.3 | 0.4 | 0.5 | 0.6 | 0.5 | 1.1 | 1.3 | 1.8 | 0.4 | 0.6 | 0.7 | 0.9 | 0.3 | 0.4 | 0.5 | 0.6
CHIEV | CHIEV150 | 150 | 3.7514 | 50.5816 | 7.2 | 30.2 | 59.1 | 109.8 | 5.7 | 19 | 36.5 | 95.6 | 12.5 | 38 | 51.1 | 115.2 | 6.7 | 22 | 48.7 | 175 | 5.7 | 19 | 36.5 | 60.5
CHINY | CHINY 70 | 70 | 5.3482 | 49.7148 | 0.4 | 0.7 | 1.1 | 7.7 | 0.4 | 0.6 | 0.8 | 2.8 | 0.5 | 1 | 1.3 | 1.9 | 0.5 | 2.7 | 5.3 | 15.6 | 0.4 | 0.6 | 0.8 | 2.8
CHOME | CHOME 36 | 36 | 4.3254 | 50.8387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CIERR | CIERR 70 | 70 | 5.9134 | 50.2496 | 1.2 | 27.8 | 48.6 | 50 | 1.1 | 1.5 | 1.8 | 3.2 | 1.2 | 3.4 | 4.4 | 6.5 | 1.3 | 1.9 | 2.2 | 3 | 1.1 | 1.5 | 1.8 | 3.2
CLANG | CLANG 36 | 36 | 3.7442 | 51.1148 | 7.6 | 60 | 60 | 60 | 1.1 | 60 | 60 | 60 | 1.1 | 60 | 60 | 60 | 1.4 | 60 | 60 | 60 | 1.1 | 9.3 | 12.2 | 25.7
COURC | COURC380 | 380 | 4.3476 | 50.4946 | 38.9 | 72.6 | 163.4 | 300 | 81.6 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 101.9 | 300 | 300 | 300 | 38.9 | 62.8 | 93.7 | 300
COUVI | COUVI 70 | 70 | 4.4991 | 50.0663 | 1.4 | 17.6 | 34.5 | 49.3 | 0.4 | 0.9 | 4.8 | 31.3 | 0.5 | 9.6 | 22.7 | 50 | 0.5 | 0.7 | 0.9 | 1.8 | 0.4 | 0.9 | 4.8 | 31.3
CQUIN | CQUIN 36 | 36 | 4.3822 | 50.8504 | 3.6 | 11.6 | 12.9 | 16.6 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 3.6 | 11.2 | 12.2 | 14.7
CQUIN | CQUIN150 | 150 | 4.3822 | 50.8504 | 7.2 | 11.6 | 12.9 | 16.6 | 31.8 | 175 | 175 | 175 | 72.9 | 175 | 175 | 175 | 44.2 | 150.7 | 175 | 175 | 7.2 | 11.2 | 12.2 | 14.7
CROIX | CROIX 70 | 70 | 5.2541 | 50.5746 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DAMPR | DAMPR150 | 150 | 4.4132 | 50.4124 | 10.5 | 21.4 | 27.7 | 46.2 | 14.2 | 74.1 | 153.3 | 175 | 25.5 | 118.4 | 175 | 175 | 35.8 | 89.4 | 166.2 | 175 | 10.5 | 19.9 | 24 | 34.5
DEUXA | DEUXA 70 | 70 | 3.853 | 50.7268 | 4.1 | 9.6 | 11.5 | 19.3 | 2 | 3.3 | 50 | 50 | 5.6 | 50 | 50 | 50 | 1.9 | 50 | 50 | 50 | 2 | 3.3 | 11.5 | 13.5
DHANI | DHANI 36 | 36 | 4.3985 | 50.8286 | 4.3 | 20 | 20 | 20 | 8.5 | 19 | 20 | 20 | 11.4 | 20 | 20 | 20 | 11.7 | 20 | 20 | 20 | 4 | 19 | 20 | 20
DHANI | DHANI150 | 150 | 4.3985 | 50.8286 | 11.5 | 36.3 | 82.9 | 175 | 8.5 | 19 | 24.3 | 33 | 11.4 | 26.3 | 46.1 | 71.1 | 11.7 | 38.8 | 57.8 | 85.8 | 6 | 19 | 23.5 | 33
DIEST | DIEST 70 | 70 | 5.0465 | 50.9927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
DILBE | DILBE 36 | 36 | 4.2574 | 50.8571 | 11.7 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 11.7 | 20 | 20 | 20
DOEL | DOEL 150 | 150 | 4.2559 | 51.3223 | 83.4 | 153.6 | 175 | 175 | 118.8 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 172.4 | 175 | 175 | 175 | 80.6 | 152.7 | 175 | 175
DOEL | DOEL 380 | 380 | 4.2559 | 51.3223 | 85.1 | 154.4 | 187 | 300 | 118.8 | 300 | 300 | 300 | 264.2 | 300 | 300 | 300 | 185.2 | 300 | 300 | 300 | 82.3 | 153.4 | 185 | 300
DORIN | DORIN 70 | 70 | 4.9805 | 50.3061 | 0.6 | 1.3 | 5.3 | 21.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.5 | 1.2 | 1.6 | 2.3 | 0.4 | 0.5 | 0.6 | 0.9 | 0.3 | 0.4 | 0.5 | 0.6
DROGE | DROGE 36 | 36 | 4.2995 | 50.8035 | 3.3 | 15.9 | 18.9 | 25 | 7.7 | 16.6 | 18.3 | 21.7 | 8.1 | 27.5 | 36.4 | 55.8 | 10.3 | 23.5 | 28.4 | 39.2 | 3.2 | 14.5 | 17.3 | 21.7
DROGE | DROGE150 | 150 | 4.2995 | 50.8035 | 11.4 | 33.9 | 78.8 | 175 | 8.5 | 36.5 | 128.9 | 175 | 16.8 | 39.3 | 99.3 | 175 | 11.7 | 82.8 | 175 | 175 | 6 | 19.5 | 23.4 | 38.5
DRONG | DRONG 36 | 36 | 3.595 | 51.0401 | 0.5 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0.5 | 20 | 20 | 20
DUINB | DUINB 36 | 36 | 3.2601 | 51.3398 | 0 | 7.1 | 18.7 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0 | 0 | 0 | 4.3
EEKLN | EEKLN 36 | 36 | 3.5376 | 51.2066 | 11.5 | 28.9 | 52.6 | 60 | 6.3 | 41.3 | 60 | 60 | 59.2 | 60 | 60 | 60 | 10.3 | 60 | 60 | 60 | 4.2 | 13.6 | 17.8 | 41.4
EEKLN | EEKLN150 | 150 | 3.5376 | 51.2066 | 11.5 | 28.9 | 52.6 | 110.4 | 8.2 | 139.3 | 175 | 175 | 60.4 | 175 | 175 | 175 | 22.3 | 175 | 175 | 175 | 7.3 | 20.6 | 31.1 | 82.6
EEKLO | EEKLO 36 | 36 | 3.5731 | 51.1745 | 0.7 | 24.5 | 33.2 | 42.8 | 0.6 | 41 | 55.5 | 60 | 1 | 21.4 | 27.9 | 50.2 | 20 | 60 | 60 | 60 | 0.6 | 9.2 | 12.1 | 27.4
EHEIN | EHEIN 70 | 70 | 5.3908 | 50.573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EISDI | EISDI 70 | 70 | 5.7118 | 51.0062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EKERE | EKERE150 | 150 | 4.4227 | 51.2888 | 4.3 | 5.4 | 6 | 6.8 | 5.9 | 12.1 | 24.7 | 61.6 | 7.6 | 13.8 | 16.7 | 27.7 | 6.8 | 26.7 | 43 | 137.3 | 4.3 | 5.1 | 5.6 | 6.5
ENGIS | ENGIS 70 | 70 | 5.3739 | 50.5666 | 1.5 | 3.2 | 8.8 | 38.3 | 1.7 | 30.2 | 46.4 | 50 | 2.8 | 50 | 50 | 50 | 2.3 | 47.6 | 50 | 50 | 1.5 | 2.3 | 3.4 | 19.2
ERTVE | ERTVE 36 | 36 | 3.7568 | 51.1771 | 7.6 | 20 | 20 | 20 | 0.7 | 20 | 20 | 20 | 0.7 | 20 | 20 | 20 | 0.7 | 20 | 20 | 20 | 0.7 | 9.2 | 12.1 | 20
ESNEU | ESNEU 70 | 70 | 5.5996 | 50.5286 | 0.7 | 1.2 | 2.3 | 18.3 | 0.7 | 6.8 | 13 | 50 | 1.2 | 50 | 50 | 50 | 1 | 37.3 | 50 | 50 | 0.7 | 1.2 | 1.9 | 13.3
ESPIN | ESPIN 36 | 36 | 4.3824 | 50.7579 | 2.8 | 4.4 | 5.4 | 10 | 4.8 | 16.9 | 20 | 20 | 10.2 | 20 | 20 | 20 | 5.3 | 11.8 | 20 | 20 | 2.7 | 4.1 | 4.6 | 6.1
ESSEG | ESSEG 36 | 36 | 4.3365 | 50.881 | 0.8 | 11.6 | 12.9 | 16.5 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0.8 | 11.2 | 12.2 | 14.7
ESSNE | ESSNE 70 | 70 | 4.125 | 50.8939 | 1.8 | 9.2 | 22 | 39.6 | 1.4 | 26.8 | 36.7 | 50 | 14 | 48.7 | 50 | 50 | 7.4 | 34.1 | 50 | 50 | 1.4 | 2 | 2.2 | 2.6
EUPEN | EUPEN 70 | 70 | 6.0217 | 50.6311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FAYSV | FAYSV 70 | 70 | 5.1596 | 49.8636 | 0.4 | 0.8 | 1.8 | 12.9 | 0.4 | 0.6 | 0.8 | 3.6 | 0.5 | 1 | 1.3 | 1.9 | 0.5 | 0.8 | 1 | 1.8 | 0.4 | 0.6 | 0.8 | 3.6
FLORA | FLORA 36 | 36 | 3.7493 | 51.0211 | 1 | 1.9 | 4.2 | 15.7 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1 | 1.9 | 3.9 | 14.7
FLORE | FLORE 70 | 70 | 5.0809 | 50.3862 | 1.4 | 2.5 | 6.4 | 42.3 | 0.7 | 5.4 | 11.3 | 44.1 | 1.2 | 19.9 | 50 | 50 | 0.8 | 1.5 | 3.1 | 14 | 0.7 | 2.1 | 3.5 | 18.2
FOOZ | FOOZ 70 | 70 | 5.436 | 50.6854 | 1.6 | 3.5 | 9.7 | 39.2 | 1.1 | 24.7 | 43.6 | 50 | 1.1 | 50 | 50 | 50 | 2.2 | 36 | 50 | 50 | 1.1 | 3.2 | 9.4 | 28.1
FORES | FORES150 | 150 | 4.3268 | 50.8076 | 7.8 | 37.8 | 84.7 | 175 | 8.5 | 19 | 23.6 | 31.4 | 11.4 | 26.2 | 46.1 | 70.9 | 11.7 | 33.1 | 45.3 | 71.2 | 5.2 | 19 | 23.6 | 31.4
GASTH | GASTH 70 | 70 | 4.6745 | 50.8843 | 1.5 | 9.3 | 12.5 | 16.2 | 22.5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 39 | 50 | 50 | 50 | 1.5 | 6.5 | 9.4 | 14.1
GEEL | GEEL 70 | 70 | 4.9425 | 51.1348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
GEMBL | GEMBL 70 | 70 | 4.6636 | 50.5506 | 0.4 | 0.8 | 3 | 17.8 | 0.4 | 0.6 | 0.7 | 1.3 | 0.6 | 1.4 | 2.6 | 25.1 | 0.5 | 0.7 | 0.9 | 1.3 | 0.4 | 0.6 | 0.7 | 1.3
GERDI | GERDI 70 | 70 | 5.5813 | 51.1391 | 2.8 | 24.9 | 35.1 | 50 | 9.2 | 26.8 | 50 | 50 | 50 | 50 | 50 | 50 | 13.8 | 50 | 50 | 50 | 2.5 | 17.8 | 26.1 | 39.2
GEZEL | GEZEL380 | 380 | 3.2012 | 51.2639 | 58.9 | 300 | 300 | 300 | 22.6 | 48.2 | 111.4 | 300 | 39.4 | 300 | 300 | 300 | 23.1 | 43.9 | 60.6 | 145.3 | 22.6 | 48.2 | 111.4 | 300
GISTE | GISTE 36 | 36 | 2.9545 | 51.1509 | 7.5 | 20 | 20 | 20 | 3 | 20 | 20 | 20 | 7.3 | 20 | 20 | 20 | 3.7 | 20 | 20 | 20 | 1.1 | 1.4 | 1.6 | 2
GODSH | GODSH 70 | 70 | 5.3746 | 50.9257 | 3.2 | 18.9 | 25.1 | 39.2 | 7.7 | 22 | 50 | 50 | 50 | 50 | 50 | 50 | 11.6 | 50 | 50 | 50 | 1.6 | 22 | 32.3 | 49.9
GODSH | GODSH150 | 150 | 5.3746 | 50.9257 | 12 | 22.6 | 26 | 35.4 | 36.8 | 175 | 175 | 175 | 51.9 | 175 | 175 | 175 | 146.7 | 175 | 175 | 175 | 11.8 | 21.6 | 24 | 29.7
GOUY | GOUY 150 | 150 | 4.3322 | 50.4826 | 14.6 | 25 | 33.7 | 77.2 | 23.9 | 86.9 | 117.1 | 173.8 | 69.4 | 300 | 300 | 300 | 35.9 | 80.4 | 167.1 | 300 | 14.5 | 21.3 | 28.5 | 63.8
GOUY | GOUY 70 | 70 | 4.3322 | 50.4826 | 1.5 | 25.5 | 34.3 | 60 | 11.4 | 28.9 | 53.9 | 60 | 60 | 60 | 60 | 60 | 16.7 | 36.4 | 60 | 60 | 1.5 | 21.3 | 28.7 | 51.2
GRAMM | GRAMM150 | 150 | 5.2865 | 50.5123 | 7.8 | 19.6 | 41.1 | 112.7 | 7.3 | 11.8 | 19.2 | 50.1 | 9.5 | 37.2 | 60.5 | 155.6 | 8.7 | 19 | 36.2 | 94.9 | 7.3 | 11.8 | 19.2 | 50.1
GRAMM | GRAMM380 | 380 | 5.2865 | 50.5123 | 67 | 300 | 300 | 300 | 42.5 | 253.5 | 300 | 300 | 255.7 | 300 | 300 | 300 | 54.9 | 300 | 300 | 300 | 42.5 | 253.5 | 300 | 300
HAM | HAM 36 | 36 | 3.7351 | 51.0605 | 7.6 | 60 | 60 | 60 | 2.6 | 60 | 60 | 60 | 57.9 | 60 | 60 | 60 | 4.2 | 60 | 60 | 60 | 2.6 | 9.4 | 12.7 | 29.7
HANNU | HANNU150 | 150 | 5.0921 | 50.6742 | 3.5 | 39.2 | 54.8 | 114.3 | 3.3 | 5.5 | 11.5 | 75.2 | 5.7 | 124.3 | 175 | 175 | 3.7 | 6.7 | 12.5 | 66 | 3.3 | 5.5 | 11.5 | 55.6
HANZI | HANZI 70 | 70 | 4.5584 | 50.2867 | 1.9 | 8.9 | 28 | 46.5 | 1.1 | 42 | 50 | 50 | 1.8 | 31.9 | 50 | 50 | 1.2 | 6.6 | 38 | 50 | 1.1 | 7.7 | 22.1 | 38.9
HAREL | HAREL 36 | 36 | 3.3123 | 50.8665 | 1.2 | 30 | 60 | 60 | 6.4 | 60 | 60 | 60 | 53.9 | 60 | 60 | 60 | 34.2 | 60 | 60 | 60 | 1.2 | 28.9 | 55.3 | 60
HARMI | HARMI 70 | 70 | 4.0193 | 50.415 | 5.1 | 33.4 | 42.5 | 50 | 1.6 | 2.8 | 5.3 | 33.2 | 3.1 | 50 | 50 | 50 | 1.9 | 2.8 | 3.4 | 5.2 | 1.6 | 2.8 | 5.3 | 33.2
HARMI | HARMI150 | 150 | 4.0193 | 50.415 | 5.1 | 33.4 | 42.5 | 75.6 | 1.6 | 2.8 | 5.3 | 33.2 | 3.1 | 72.7 | 107.9 | 161.5 | 1.9 | 2.8 | 3.4 | 5.2 | 1.6 | 2.8 | 5.3 | 33.2
HARYD | HARYD 36 | 36 | 4.4245 | 50.8891 | 4.7 | 10.7 | 12.1 | 15.5 | 1.1 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 1.3 | 20 | 20 | 20 | 1.1 | 6.4 | 8.5 | 13.1
HASTI | HASTI 70 | 70 | 4.8201 | 50.2118 | 0.4 | 1.9 | 4.5 | 10.2 | 0.4 | 4 | 7.2 | 11.6 | 0.5 | 5.2 | 16.5 | 27.8 | 0.5 | 0.9 | 1.8 | 12.6 | 0.4 | 1 | 2.7 | 8.5
HAVE7 | HAVE7150 | 150 | 4.3865 | 51.2879 | 4.2 | 4.9 | 5.2 | 6 | 12.8 | 17.4 | 23.2 | 57.7 | 16.2 | 33.1 | 44.3 | 68.7 | 14.1 | 25 | 40.3 | 128.7 | 4.2 | 4.9 | 5.1 | 5.8
HECHT | HECHT 70 | 70 | 5.3931 | 51.1303 | 4.6 | 20 | 28.2 | 39.5 | 6.5 | 15.2 | 50 | 50 | 50 | 50 | 50 | 50 | 9.7 | 50 | 50 | 50 | 3.7 | 11.9 | 21.4 | 30.5
HEID | HEID 70 | 70 | 5.7176 | 50.4561 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HEIMO | HEIMO150 | 150 | 4.136 | 51.1414 | 3.6 | 13.8 | 19.5 | 52 | 11 | 13.3 | 14.5 | 17.8 | 19.6 | 61.6 | 80.2 | 126.3 | 12.7 | 19.2 | 23.5 | 32.8 | 3.2 | 12.3 | 14.5 | 17.8
HEINS | HEINS 70 | 70 | 5.7552 | 49.6935 | 1.2 | 3.6 | 9.2 | 41.4 | 1.7 | 3.3 | 6 | 17.9 | 2.2 | 5.2 | 7.8 | 14 | 2.9 | 13.4 | 25 | 50 | 1.2 | 2.4 | 3 | 5.8
HEINS | HEINS220 | 220 | 5.7552 | 49.6935 | 4.4 | 6.3 | 9.5 | 55.7 | 4.4 | 7.4 | 15.8 | 175 | 14.4 | 175 | 175 | 175 | 6 | 24.9 | 81.4 | 175 | 4.4 | 6.3 | 9.5 | 50.9
HELIA | HELIA 36 | 36 | 4.3517 | 50.8586 | 11.6 | 20 | 20 | 20 | 2.7 | 20 | 20 | 20 | 17 | 20 | 20 | 20 | 3.2 | 20 | 20 | 20 | 2.7 | 20 | 20 | 20
HELIB | HELIB 36 | 36 | 4.3517 | 50.8586 | 3.9 | 11.6 | 12.9 | 16.5 | 3.4 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 4.9 | 20 | 20 | 20 | 2.1 | 11.2 | 12.2 | 14.7
HELIP | HELIP150 | 150 | 4.3517 | 50.8586 | 11.6 | 25.1 | 38.3 | 114.4 | 31.8 | 116.4 | 124.8 | 175 | 100.2 | 175 | 175 | 175 | 50.2 | 166.7 | 175 | 175 | 3.3 | 20.8 | 31.5 | 78
HEOUT | HEOUT 70 | 70 | 4.7986 | 51.1563 | 0.6 | 3.9 | 11.2 | 30 | 10.7 | 27.2 | 33.3 | 50 | 44.2 | 50 | 50 | 50 | 17.3 | 50 | 50 | 50 | 0.6 | 3.7 | 11.2 | 34
HERBA | HERBA 70 | 70 | 5.5503 | 50.0494 | 0.3 | 2.5 | 4.6 | 17.1 | 0.3 | 1.1 | 2.4 | 9.6 | 0.5 | 1 | 1.2 | 2.2 | 0.5 | 1.9 | 4.8 | 10 | 0.3 | 1.1 | 2.4 | 9.6
HEREN | HEREN 70 | 70 | 4.8683 | 51.1796 | 5.2 | 7.3 | 10.1 | 32.2 | 2.6 | 26.9 | 32.9 | 50 | 35.8 | 50 | 50 | 50 | 2.8 | 46.8 | 50 | 50 | 2.6 | 7.3 | 9.7 | 23.3
HEREN | HEREN150 | 150 | 4.8683 | 51.1796 | 2.3 | 3.3 | 4.8 | 19.2 | 6.9 | 26.8 | 33.1 | 53 | 36.4 | 175 | 175 | 175 | 16.3 | 47.5 | 63.4 | 102.9 | 2.3 | 3.3 | 4.8 | 12.4
HERST | HERST 70 | 70 | 5.6286 | 50.6779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HEULE | HEULE 70 | 70 | 3.2489 | 50.8335 | 2.5 | 4.1 | 6.6 | 36.9 | 2.5 | 50 | 50 | 50 | 3.3 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1.3 | 5.5 | 14.5 | 31.7
HEVRL | HEVRL 70 | 70 | 4.7184 | 50.8548 | 1.5 | 9 | 12 | 16.2 | 34.6 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1.5 | 6.2 | 9.2 | 14
HEZE | HEZE 150 | 150 | 4.9446 | 51.1369 | 4.9 | 7.4 | 9.7 | 23 | 11.2 | 24.2 | 29.9 | 43.2 | 28.4 | 119.3 | 175 | 175 | 12.1 | 41.3 | 54.6 | 90 | 4.9 | 7.5 | 10.1 | 24
HOBOK | HOBOK 70 | 70 | 4.3433 | 51.1586 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HOLLO | HOLLO 70 | 70 | 5.4952 | 50.6548 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HOOGS | HOOGS 36 | 36 | 4.7503 | 51.3902 | 4.5 | 20 | 20 | 20 | 4.1 | 8.7 | 14.3 | 20 | 7.2 | 15.5 | 20 | 20 | 5.6 | 16.8 | 20 | 20 | 4.1 | 8.7 | 14.3 | 20
HORTA | HORTA380 | 380 | 3.6037 | 51.1146 | 65.7 | 300 | 300 | 300 | 72.2 | 203.8 | 300 | 300 | 212.9 | 300 | 300 | 300 | 82.2 | 161.5 | 275.2 | 300 | 65.7 | 203.8 | 300 | 300
HOUFF | HOUFF 70 | 70 | 5.7951 | 50.1501 | 6.1 | 11 | 14.7 | 38.3 | 0.5 | 0.7 | 0.8 | 1.3 | 0.6 | 1.8 | 2.4 | 4 | 0.6 | 0.9 | 1.1 | 1.5 | 0.5 | 0.7 | 0.8 | 1.3
HOUTH | HOUTH 70 | 70 | 5.3713 | 51.0295 | 3.5 | 16 | 23.4 | 34.9 | 5.4 | 12.6 | 50 | 50 | 24.9 | 50 | 50 | 50 | 8.1 | 50 | 50 | 50 | 2.9 | 9.2 | 18.4 | 25.8
HOUTW | HOUTW 36 | 36 | 4.4157 | 50.882 | 4.7 | 10.7 | 12.1 | 15.5 | 18.6 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0.3 | 6.4 | 8.5 | 13.1
HOVES | HOVES 70 | 70 | 4.0316 | 50.6795 | 1 | 3.3 | 5.4 | 11.7 | 1.2 | 3.3 | 4.6 | 6.2 | 4.3 | 16.5 | 21.2 | 31.8 | 1.5 | 2.8 | 4.3 | 7 | 0.9 | 2.2 | 3.4 | 6.2
HULDN | HULDN 36 | 36 | 4.5999 | 50.7815 | 0.5 | 4.8 | 5.5 | 7.9 | 4.4 | 16.2 | 20 | 20 | 7.5 | 20 | 20 | 20 | 5.6 | 13.6 | 20 | 20 | 0.5 | 4.7 | 5.3 | 7
IEPER | IEPER150 | 150 | 2.8594 | 50.8477 | 3.2 | 34.9 | 66.6 | 101.2 | 24.9 | 175 | 175 | 175 | 136.1 | 175 | 175 | 175 | 34.3 | 175 | 175 | 175 | 3 | 27.1 | 53.4 | 80.6
IVOZ | IVOZ 70 | 70 | 5.4604 | 50.5933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
IXELL | IXELL 36 | 36 | 4.3949 | 50.8141 | 4.2 | 36.9 | 60 | 60 | 8.5 | 19 | 23.6 | 31.4 | 11.4 | 26.2 | 46.1 | 60 | 11.7 | 32.9 | 45 | 60 | 4 | 19 | 23.6 | 31.4
IXELL | IXELL150 | 150 | 4.3949 | 50.8141 | 11.5 | 36.9 | 84.1 | 175 | 8.5 | 19 | 23.6 | 31.4 | 11.4 | 26.2 | 46.1 | 71 | 11.7 | 32.9 | 45 | 71.1 | 6 | 19 | 23.5 | 31.4
IZGEM | IZGEM150 | 150 | 3.2264 | 50.8972 | 13.3 | 36.6 | 122 | 300 | 18.5 | 49 | 68.3 | 169 | 48.2 | 300 | 300 | 300 | 24.3 | 60.3 | 76.8 | 121.2 | 13.3 | 34.1 | 68.3 | 169
JEMAP | JEMAP 70 | 70 | 3.8717 | 50.4545 | 1.4 | 2.4 | 3 | 3.9 | 1.3 | 6.2 | 7.7 | 9.8 | 2.3 | 21.6 | 28.1 | 40.2 | 1.4 | 5.9 | 7.8 | 14.4 | 1.3 | 2.2 | 2.7 | 3.6
JOSAP | JOSAP 36 | 36 | 4.3931 | 50.8612 | 0.3 | 11.4 | 12.6 | 15.7 | 2.3 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0.3 | 11 | 12 | 14.3
JUPIL | JUPIL220 | 220 | 5.6196 | 50.6445 | 12.9 | 21.1 | 32 | 67.6 | 14 | 28.5 | 56.9 | 175 | 26.7 | 149.7 | 175 | 175 | 20.6 | 175 | 175 | 175 | 12.9 | 18.7 | 22.1 | 32.3
KALLO | KALLO 36 | 36 | 4.2888 | 51.2533 | 3.1 | 9.8 | 10.6 | 12.7 | 1.3 | 13.5 | 14.8 | 18.4 | 2.2 | 25.1 | 30 | 40.4 | 4.5 | 18.3 | 21.8 | 32.3 | 1.3 | 3.8 | 4.6 | 7.8
KALLO | KALLO150 | 150 | 4.2888 | 51.2533 | 4.2 | 9.8 | 10.6 | 12.7 | 7.7 | 13.5 | 14.8 | 18.4 | 13.9 | 25.1 | 30 | 40.4 | 8.3 | 18.3 | 21.8 | 36.5 | 4.2 | 6.8 | 7.4 | 9
KENNE | KENNE 36 | 36 | 3.7821 | 51.1285 | 1.2 | 16.6 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 1.2 | 6.4 | 12.5 | 20
KERSB | KERSB 70 | 70 | 4.993 | 50.8921 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KESLO | KESLO 70 | 70 | 4.7478 | 50.8865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KETEN | KETEN 36 | 36 | 4.2789 | 51.2694 | 3.1 | 9.8 | 10.6 | 12.7 | 1.3 | 13.5 | 14.8 | 18.4 | 2.2 | 25.1 | 30 | 40.4 | 4.5 | 18.3 | 21.8 | 32.3 | 1.3 | 3.8 | 4.6 | 7.8
KETEN | KETEN150 | 150 | 4.2789 | 51.2694 | 3.1 | 9.8 | 10.6 | 12.7 | 7.7 | 13.5 | 14.8 | 18.4 | 13.9 | 25.1 | 30 | 40.4 | 8.3 | 18.3 | 21.8 | 32.4 | 3.1 | 3.8 | 4.6 | 7.8
KOKSI | KOKSI150 | 150 | 2.6751 | 51.1105 | 10.8 | 44.8 | 81.8 | 175 | 4.5 | 62 | 81.8 | 112 | 11.1 | 175 | 175 | 175 | 5.9 | 68.4 | 110.8 | 166.3 | 4.5 | 22 | 50.4 | 109.3
KONTI | KONTI 70 | 70 | 4.4695 | 51.1188 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
KOOST | KOOST 70 | 70 | 3.2942 | 50.8258 | 2.7 | 21.7 | 29.3 | 37.3 | 2.5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 36.3 | 50 | 50 | 50 | 1.2 | 5.8 | 15 | 29
KUURN | KUURN 70 | 70 | 3.264 | 50.8593 | 2.3 | 3.8 | 6.1 | 37.3 | 2.5 | 50 | 50 | 50 | 3.1 | 50 | 50 | 50 | 35.9 | 50 | 50 | 50 | 1.4 | 5.1 | 13.8 | 29.2
KWATW | KWATW 36 | 36 | 3.8285 | 50.9929 | 1 | 1.9 | 4.2 | 16.3 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0.7 | 1.9 | 3.9 | 14.7
LACRO | LACRO150 | 150 | 4.1917 | 50.4941 | 5.4 | 19.4 | 27.1 | 49.6 | 2.8 | 54 | 74.1 | 115.4 | 30.9 | 175 | 175 | 175 | 35.1 | 72.9 | 149.1 | 175 | 2.8 | 18.5 | 23.7 | 35.9
LANAI | LANAI 70 | 70 | 5.6607 | 50.8873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LANAK | LANAK150 | 150 | 5.6435 | 50.8834 | 9.1 | 25.4 | 45.5 | 174 | 53.1 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 86.1 | 175 | 175 | 175 | 9.1 | 25 | 31.5 | 40.7
LANDN | LANDN 70 | 70 | 5.0701 | 50.7514 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LANGE | LANGE150 | 150 | 3.7412 | 51.1162 | 7.6 | 100.2 | 163.2 | 175 | 35.3 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 91.5 | 175 | 175 | 175 | 5.9 | 9.3 | 12.2 | 26.2
LANLO | LANLO 70 | 70 | 5.512 | 50.9384 | 9.5 | 29.9 | 46.6 | 60 | 9.4 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 10.1 | 60 | 60 | 60 | 1.6 | 27.4 | 60 | 60
LANLO | LANLO150 | 150 | 5.512 | 50.9384 | 9.1 | 30.7 | 48.2 | 175 | 110.7 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 9.1 | 26.5 | 40.5 | 110.7
LATOU | LATOU 70 | 70 | 5.5856 | 49.5487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LENS | LENS 70 | 70 | 3.9031 | 50.5651 | 1.1 | 3.9 | 4.9 | 6.5 | 1.1 | 5 | 7.4 | 11.9 | 1.9 | 9.5 | 13.3 | 24.2 | 1.6 | 5.1 | 7 | 11.4 | 1 | 2.3 | 2.9 | 3.9
LEUZE | LEUZE 70 | 70 | 4.9119 | 50.5518 | 1.1 | 5.8 | 12.6 | 50 | 0.7 | 1.5 | 4.3 | 21.9 | 1.4 | 7.3 | 24.5 | 50 | 0.8 | 1.2 | 1.6 | 3.5 | 0.7 | 1.5 | 4.3 | 21.9
LEVAL | LEVAL220 | 220 | 5.4927 | 50.6042 | 12.8 | 31.4 | 47.8 | 119.8 | 7.2 | 18 | 38.1 | 175 | 12.8 | 175 | 175 | 175 | 18.1 | 175 | 175 | 175 | 7.2 | 18 | 27.3 | 38.5
LIBER | LIBER 70 | 70 | 4.4296 | 50.5151 | 4.5 | 18.5 | 25.9 | 37.1 | 0.3 | 0.4 | 0.5 | 0.6 | 0.5 | 1.1 | 1.3 | 1.8 | 0.4 | 0.6 | 0.7 | 0.9 | 0.3 | 0.4 | 0.5 | 0.6
LICHT | LICHT 36 | 36 | 3.1223 | 51.0248 | 0.2 | 1.8 | 2.6 | 3.5 | 0 | 20 | 20 | 20 | 0 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0 | 1.8 | 2.5 | 3.5
LIER | LIER 70 | 70 | 4.5566 | 51.1339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LIGNE | LIGNE 70 | 70 | 3.7014 | 50.6274 | 1.5 | 4.3 | 6.6 | 11.4 | 1.8 | 3 | 3.7 | 5.6 | 6.6 | 19.7 | 22.6 | 29.4 | 2 | 4.1 | 5.6 | 9.1 | 1.5 | 3 | 3.7 | 5.6
LILLA | LILLA 36 | 36 | 4.3073 | 51.3011 | 1.1 | 4.3 | 10.4 | 20 | 11.1 | 20 | 20 | 20 | 17.7 | 20 | 20 | 20 | 11.4 | 20 | 20 | 20 | 0.9 | 1.7 | 2.4 | 8.7
LILLB | LILLB 36 | 36 | 4.3073 | 51.3011 | 0.9 | 4.2 | 10.3 | 20 | 11.1 | 20 | 20 | 20 | 17.7 | 20 | 20 | 20 | 11.4 | 20 | 20 | 20 | 0.9 | 1.7 | 2.4 | 8.6
LILLO | LILLO150 | 150 | 4.307 | 51.3013 | 8.5 | 102.3 | 137.2 | 196 | 7.7 | 104.4 | 130.5 | 175.8 | 53 | 292.8 | 300 | 300 | 8.3 | 160.1 | 244.9 | 300 | 7.7 | 99 | 125.3 | 170.3
LILLO | LILLO380 | 380 | 4.307 | 51.3013 | 83.3 | 153.6 | 185.2 | 300 | 127.6 | 300 | 300 | 300 | 281.3 | 300 | 300 | 300 | 185.2 | 300 | 300 | 300 | 80.5 | 151.4 | 179.6 | 276.3
LINT | LINT 150 | 150 | 4.5087 | 51.1176 | 13.2 | 43.2 | 90.1 | 158 | 9.2 | 21.3 | 42.1 | 145.3 | 16.7 | 46 | 58.3 | 105.8 | 11.1 | 24 | 52.5 | 199.1 | 9.2 | 15.6 | 42.1 | 118.9
LIXHE | LIXHE 70 | 70 | 5.6692 | 50.754 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LIXHE | LIXHE150 | 150 | 5.6692 | 50.754 | 7.5 | 19.8 | 45.7 | 76.8 | 8.5 | 46 | 69.4 | 209.2 | 26.4 | 60.7 | 101.1 | 300 | 19.4 | 182.3 | 276.2 | 300 | 7.5 | 19.8 | 34.8 | 49.5
LIXHE | LIXHE220 | 220 | 5.6692 | 50.754 | 9.2 | 15.8 | 25.9 | 61.3 | 9.2 | 18.3 | 33.7 | 163.5 | 17.3 | 96.9 | 175 | 175 | 11 | 114.6 | 175 | 175 | 9.2 | 14.2 | 18.1 | 30.8
LIXHE | LIXHE380 | 380 | 5.6692 | 50.754 | 37.9 | 76.5 | 146.2 | 300 | 24.9 | 242.5 | 300 | 300 | 193.6 | 300 | 300 | 300 | 36 | 284.1 | 300 | 300 | 24.9 | 57.5 | 91.9 | 300
LOBBE | LOBBE 70 | 70 | 4.2607 | 50.3582 | 1.5 | 17.1 | 33.6 | 50 | 11 | 30.6 | 50 | 50 | 38.6 | 50 | 50 | 50 | 16.7 | 36.4 | 50 | 50 | 1.5 | 11.2 | 28.6 | 48.4
LOEWP | LOEWP 36 | 36 | 4.7162 | 51.445 | 4.3 | 20 | 20 | 20 | 4.1 | 8.6 | 13.3 | 20 | 7.2 | 15.4 | 19.7 | 20 | 5.6 | 15.1 | 20 | 20 | 4.1 | 8.6 | 13.3 | 20
LOKER | LOKER 36 | 36 | 3.9799 | 51.1062 | 8 | 13.8 | 20 | 20 | 11 | 13.3 | 14.6 | 18 | 20 | 20 | 20 | 20 | 12.7 | 19.2 | 20 | 20 | 3.2 | 12 | 14.6 | 18
LOMME | LOMME150 | 150 | 5.2667 | 51.2364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LOUVA | LOUVA 36 | 36 | 4.6186 | 50.6708 | 1 | 4.8 | 5.7 | 8.8 | 1.9 | 16.6 | 20 | 20 | 7.5 | 20 | 20 | 20 | 2.7 | 20 | 20 | 20 | 1 | 4.6 | 5.3 | 7.5
LUMME | LUMME 70 | 70 | 5.2282 | 50.9909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MAASE | MAASE 70 | 70 | 5.7844 | 51.0922 | 1.5 | 33.1 | 46.6 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1.3 | 21.5 | 31 | 45.9
MAASM | MAASM 70 | 70 | 5.6954 | 50.9476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MACHE | MACHE 36 | 36 | 4.4275 | 50.9172 | 4.7 | 10.7 | 11.9 | 14.4 | 25.4 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 35.3 | 60 | 60 | 60 | 4.7 | 6.4 | 8.5 | 12.9
MACHE | MACHE150 | 150 | 4.4275 | 50.9172 | 4.7 | 10.7 | 11.9 | 14.4 | 25.4 | 175 | 175 | 175 | 72.9 | 175 | 175 | 175 | 35.3 | 175 | 175 | 175 | 4.7 | 6.4 | 8.5 | 12.9
MAERL | MAERL380 | 380 | 3.3158 | 51.227 | 58.9 | 300 | 300 | 300 | 40.2 | 182.5 | 300 | 300 | 176.2 | 300 | 300 | 300 | 48.7 | 198.4 | 300 | 300 | 40.2 | 182.5 | 300 | 300
MAGOT | MAGOT 70 | 70 | 5.6352 | 50.6062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MALDR | MALDR 70 | 70 | 4.2649 | 51.022 | 1.9 | 20.8 | 29.4 | 58.7 | 17.7 | 60 | 60 | 60 | 37.8 | 60 | 60 | 60 | 25.8 | 60 | 60 | 60 | 1.6 | 2 | 2.6 | 8.6
MALEC | MALEC150 | 150 | 4.2218 | 50.556 | 5.3 | 22.1 | 30.3 | 58.3 | 7.8 | 70.2 | 92.4 | 130.5 | 40 | 175 | 175 | 175 | 33.9 | 75.3 | 156.8 | 175 | 5 | 20 | 25.7 | 37.7
MARCO | MARCO 70 | 70 | 5.5502 | 50.21 | 0.7 | 3.7 | 10.4 | 26.7 | 1 | 5.7 | 15.3 | 45.1 | 3.2 | 6 | 7.9 | 13.8 | 1.1 | 10.5 | 19.3 | 49 | 0.7 | 3.7 | 8.5 | 23.6
MARFA | MARFA 70 | 70 | 5.3454 | 50.2369 | 1 | 2.2 | 3.8 | 9.5 | 1.9 | 7.9 | 11.5 | 42 | 2.3 | 20.9 | 40.7 | 50 | 2 | 5.2 | 15.4 | 50 | 1 | 2.1 | 4 | 11.9
MARLD | MARLD 70 | 70 | 4.9744 | 50.4795 | 1.1 | 2.7 | 4.2 | 24.8 | 0.6 | 4 | 24.2 | 45.7 | 1 | 8.1 | 35.2 | 50 | 0.7 | 2.5 | 3.9 | 7.6 | 0.6 | 2.3 | 3.2 | 6.6
MASSE | MASSE150 | 150 | 4.6292 | 51.1958 | 7.5 | 49.8 | 136.8 | 175 | 6.8 | 14.3 | 22.4 | 118.4 | 11.1 | 29.7 | 42.5 | 100.4 | 9.5 | 29.6 | 58.3 | 172.8 | 6.8 | 14.3 | 22.4 | 118.4
MASSE | MASSE380 | 380 | 4.6292 | 51.1958 | 37.7 | 136.7 | 300 | 300 | 141.6 | 300 | 300 | 300 | 258 | 300 | 300 | 300 | 205.6 | 300 | 300 | 300 | 37.7 | 131.1 | 254.3 | 300
MECHL | MECHL 70 | 70 | 4.4672 | 51.0366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MEERH | MEERH150 | 150 | 5.0632 | 51.1073 | 7.6 | 41.2 | 69.7 | 83.6 | 11.9 | 46.6 | 217.5 | 300 | 48.6 | 300 | 300 | 300 | 19 | 73.2 | 130.2 | 300 | 7.6 | 41.2 | 69.7 | 83.6
MEERH | MEERH380 | 380 | 5.0632 | 51.1073 | 45.4 | 169.7 | 300 | 300 | 161.5 | 300 | 300 | 300 | 294.8 | 300 | 300 | 300 | 234.5 | 300 | 300 | 300 | 45.4 | 155.9 | 300 | 300
MERCA | MERCA150 | 150 | 4.2468 | 51.1541 | 8.5 | 12.3 | 14.9 | 25.8 | 11 | 13.3 | 14.5 | 17.8 | 19.6 | 60.3 | 78.2 | 121.5 | 12.7 | 19.2 | 23.5 | 32.8 | 8 | 11.9 | 13.9 | 17.8
MERCA | MERCA380 | 380 | 4.2468 | 51.1541 | 83.2 | 149.9 | 180.7 | 300 | 124.5 | 300 | 300 | 300 | 257.2 | 300 | 300 | 300 | 180.8 | 300 | 300 | 300 | 80.4 | 145.2 | 166.9 | 235
MERCH | MERCH 70 | 70 | 4.2235 | 50.9653 | 1.9 | 19.8 | 42 | 50 | 1.4 | 12.5 | 28.6 | 50 | 10.9 | 50 | 50 | 50 | 2.3 | 7.8 | 28.3 | 50 | 1.4 | 2 | 2.1 | 2.6
MERKS | MERKS150 | 150 | 4.457 | 51.2398 | 5.2 | 42.8 | 99 | 175 | 7.5 | 22.5 | 43.7 | 175 | 14 | 38.8 | 56.4 | 104.3 | 12 | 37.7 | 82.8 | 175 | 5.1 | 15.8 | 43.7 | 136.1
MIDI | MIDI 150 | 150 | 4.3241 | 50.8279 | 11.6 | 37.4 | 70.7 | 120.7 | 8.5 | 19.1 | 23.7 | 31.5 | 11.4 | 26.3 | 46.2 | 71.2 | 11.7 | 33.3 | 45.5 | 71.4 | 6 | 19.1 | 23.5 | 31.5
MIDI | MIDI 36 | 36 | 4.3241 | 50.8279 | 4 | 7.9 | 8.7 | 10.3 | 3.3 | 20 | 20 | 20 | 7.6 | 20 | 20 | 20 | 4 | 20 | 20 | 20 | 3.3 | 8.2 | 9 | 10.7
MIECR | MIECR 70 | 70 | 5.2329 | 50.3698 | 1.3 | 2.5 | 4.6 | 14.9 | 0.2 | 0.3 | 0.4 | 1 | 0.4 | 1.3 | 2.3 | 7.1 | 0.3 | 0.4 | 0.5 | 0.7 | 0.2 | 0.3 | 0.4 | 1
MOARD | MOARD 70 | 70 | 4.9849 | 49.909 | 0.4 | 0.8 | 1.8 | 9.5 | 0.4 | 0.6 | 0.8 | 2.9 | 0.5 | 1 | 1.3 | 1.9 | 0.5 | 0.8 | 1.2 | 2 | 0.4 | 0.6 | 0.8 | 2.9
MOL | MOL 150 | 150 | 5.1081 | 51.2213 | 6.4 | 12 | 24.9 | 125.5 | 11.8 | 175 | 175 | 175 | 28.2 | 128.4 | 175 | 175 | 17.2 | 175 | 175 | 175 | 5.3 | 12.5 | 24.7 | 97.7
MOL | MOL 70 | 70 | 5.1081 | 51.2213 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MOLEN | MOLEN 36 | 36 | 4.3249 | 50.852 | 11.7 | 25.1 | 38.3 | 60 | 12.9 | 35.5 | 60 | 60 | 17 | 39.9 | 60 | 60 | 24.9 | 60 | 60 | 60 | 3.3 | 20.8 | 31.5 | 56.5
MOLEN | MOLEN150 | 150 | 4.3249 | 50.852 | 11.6 | 25.1 | 38.3 | 115.2 | 12.9 | 35.5 | 80.7 | 175 | 17 | 39.9 | 89.5 | 175 | 24.9 | 132.5 | 175 | 175 | 3.3 | 20.8 | 31.5 | 78
MONCE | MONCE150 | 150 | 4.3739 | 50.396 | 9 | 20.7 | 26.9 | 44.3 | 11.9 | 69.7 | 137.7 | 175 | 21.4 | 85 | 175 | 175 | 25.7 | 89.5 | 159.5 | 175 | 9 | 19.1 | 23.3 | 33.9
MONS | MONS 70 | 70 | 3.9458 | 50.4612 | 1.2 | 2.5 | 3.1 | 4.2 | 1.2 | 9.3 | 11 | 14.4 | 2 | 45.1 | 50 | 50 | 1.7 | 12.9 | 15.6 | 23.4 | 1.2 | 2.3 | 2.9 | 4
MONTE | MONTE 70 | 70 | 5.5313 | 50.6434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MONTI | MONTI150 | 150 | 4.4614 | 50.4019 | 4.8 | 13.6 | 21.7 | 35.1 | 4.9 | 54.4 | 127.4 | 175 | 8.8 | 25.6 | 62 | 175 | 7.5 | 55.1 | 135.1 | 175 | 4.7 | 10.8 | 19.6 | 28.9
MORTS | MORTS150 | 150 | 4.4698 | 51.176 | 4.7 | 60.8 | 99.7 | 175 | 9 | 37.2 | 99.5 | 175 | 17.7 | 78.6 | 174.9 | 175 | 15.3 | 47.3 | 97.8 | 175 | 3.9 | 12.4 | 56.4 | 117.3
MOUSC | MOUSC150 | 150 | 3.2477 | 50.7565 | 14.8 | 26.8 | 95.8 | 175 | 9 | 175 | 175 | 175 | 80.6 | 175 | 175 | 175 | 8.8 | 175 | 175 | 175 | 9 | 25.8 | 50.6 | 128.8
NAMUR | NAMUR 70 | 70 | 4.835 | 50.4617 | 1.1 | 4.2 | 7.5 | 27 | 1 | 5.2 | 8.4 | 16.9 | 3.7 | 50 | 50 | 50 | 1.5 | 3.7 | 6.1 | 13.1 | 1 | 3.8 | 5.7 | 16.9
NAPLE | NAPLE 36 | 36 | 4.3661 | 50.8375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NEUFC | NEUFC 70 | 70 | 5.4448 | 49.8578 | 1 | 1.9 | 3.7 | 7.5 | 0.9 | 2.2 | 3.7 | 10.4 | 1.7 | 3.2 | 3.9 | 6.7 | 1.7 | 6.4 | 11.5 | 50 | 0.9 | 1.7 | 2.9 | 6.6
NEUVI | NEUVI 70 | 70 | 4.5273 | 50.172 | 2.5 | 19.8 | 43.3 | 50 | 0.5 | 1 | 5.2 | 31.4 | 1 | 10.2 | 22.9 | 50 | 0.6 | 0.8 | 1.1 | 2 | 0.5 | 1 | 5.2 | 31.4
NIEUW | NIEUW 36 | 36 | 3.7156 | 51.068 | 7.6 | 20 | 20 | 20 | 2.6 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 4.2 | 20 | 20 | 20 | 2.6 | 9.4 | 12.7 | 20
NIEUW | NIEUW150 | 150 | 3.7156 | 51.068 | 14.2 | 104.6 | 175 | 175 | 35.3 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 114.1 | 175 | 175 | 175 | 14.2 | 25.6 | 42.6 | 105.8
NINOV | NINOV 70 | 70 | 4.0085 | 50.8422 | 1.6 | 10.4 | 16.1 | 27.5 | 1.3 | 1.6 | 1.7 | 2.1 | 2.4 | 9.1 | 11.8 | 19.5 | 1.5 | 2.2 | 2.7 | 3.9 | 1.3 | 1.6 | 1.7 | 2.1
NORDL | NORDL150 | 150 | 4.2514 | 51.3698 | 8.6 | 129.6 | 175 | 175 | 91.1 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 8.6 | 121.8 | 151.7 | 175
OISQU | OISQU 70 | 70 | 4.2247 | 50.6661 | 2.8 | 9.2 | 14.9 | 25.8 | 3.6 | 8.5 | 11.8 | 19.3 | 14.3 | 50 | 50 | 50 | 5.2 | 9 | 14.4 | 24 | 2.4 | 8.3 | 11.8 | 17.1
OISQU | OISQU150 | 150 | 4.2247 | 50.6661 | 2.6 | 4.8 | 8.1 | 15.1 | 2.8 | 14 | 72.1 | 175 | 54.1 | 175 | 175 | 175 | 3.8 | 106 | 175 | 175 | 2.6 | 4.7 | 6.9 | 9.2
ON___ | ON___ 70 | 70 | 5.2746 | 50.1677 | 0.3 | 0.8 | 2.1 | 7.5 | 0.3 | 1.3 | 9.4 | 25 | 1 | 14.1 | 28 | 50 | 0.5 | 3.3 | 10.7 | 43.5 | 0.3 | 0.8 | 2.3 | 9.1
OOSTR | OOSTR 70 | 70 | 3.3231 | 50.9133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OPGLA | OPGLA 70 | 70 | 5.5523 | 51.0397 | 2.7 | 25.6 | 43.3 | 50 | 8.7 | 25.4 | 50 | 50 | 50 | 50 | 50 | 50 | 13.1 | 50 | 50 | 50 | 2.6 | 15.3 | 25.1 | 50
ORGEO | ORGEO 70 | 70 | 5.3029 | 49.8466 | 0.4 | 0.7 | 1.4 | 9.7 | 0.4 | 0.6 | 0.8 | 2.9 | 0.5 | 1 | 1.4 | 3.1 | 0.5 | 2.6 | 4.4 | 13.7 | 0.4 | 0.6 | 0.8 | 2.9
OS1ST | OS1ST220 | 220 | 2.8687 | 51.5823 | 65.7 | 175 | 175 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OS2ST | OS2ST220 | 220 | 2.919 | 51.5755 | 65.7 | 175 | 175 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTTIG | OTTIG 36 | 36 | 4.5685 | 50.6619 | 0.5 | 4.6 | 5.6 | 9.2 | 2.4 | 16.3 | 20 | 20 | 7.5 | 20 | 20 | 20 | 4.2 | 20 | 20 | 20 | 0.5 | 4.3 | 5 | 7.1
OVERI | OVERI 70 | 70 | 5.3831 | 51.2149 | 4.3 | 20.7 | 27.8 | 50 | 7.9 | 46.6 | 50 | 50 | 50 | 50 | 50 | 50 | 11.9 | 50 | 50 | 50 | 3.2 | 17 | 25.4 | 42.1
OVERP | OVERP150 | 150 | 5.3937 | 51.2278 | 5.6 | 12 | 24.5 | 107.7 | 12.3 | 175 | 175 | 175 | 32.4 | 164 | 175 | 175 | 18.1 | 175 | 175 | 175 | 5.6 | 11.4 | 19.2 | 80.3
PACHE | PACHE150 | 150 | 4.3615 | 50.8499 | 7.3 | 11.6 | 12.9 | 16.6 | 31.8 | 175 | 175 | 175 | 72.9 | 175 | 175 | 175 | 44.2 | 150.7 | 175 | 175 | 7.2 | 11.2 | 12.2 | 14.7
PATHO | PATHO 36 | 36 | 3.2106 | 51.2537 | 6.4 | 20 | 20 | 20 | 0.6 | 18.1 | 20 | 20 | 2.7 | 20 | 20 | 20 | 0.6 | 10.5 | 17.6 | 20 | 0.6 | 18.1 | 20 | 20
PATUR | PATUR 70 | 70 | 3.8581 | 50.4025 | 0.8 | 2.7 | 3.7 | 6 | 0.8 | 5.5 | 7 | 9.2 | 1.4 | 22.7 | 27.9 | 38.1 | 1.2 | 3.8 | 6.8 | 11.7 | 0.8 | 2.6 | 3.7 | 5.9
PETRO | PETRO150 | 150 | 4.3724 | 51.202 | 4.3 | 41.6 | 87.6 | 175 | 9 | 25.8 | 44.7 | 175 | 17.8 | 40.1 | 51.2 | 92.3 | 14.3 | 38.9 | 70.2 | 175 | 3.9 | 12.9 | 44.7 | 111.6
PLATE | PLATE150 | 150 | 4.3872 | 50.1898 | 1.8 | 9.9 | 15.2 | 29.4 | 7.1 | 22.6 | 34.4 | 69.2 | 12.7 | 40.9 | 99 | 175 | 18.7 | 66.8 | 90.2 | 145.2 | 1.8 | 9.9 | 15.2 | 29.4
PLENE | PLENE 70 | 70 | 5.8768 | 50.632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PONDR | PONDR 70 | 70 | 5.0014 | 50.0955 | 0.4 | 1.9 | 4.6 | 10.5 | 0.4 | 4 | 8.3 | 23.9 | 0.5 | 4.8 | 17 | 27.8 | 0.5 | 0.9 | 1.8 | 25.4 | 0.4 | 1 | 2.6 | 9.3
PRECH | PRECH 70 | 70 | 5.8439 | 50.5994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PROFO | PROFO 70 | 70 | 5.4634 | 50.6152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PTOUE | PTOUE 36 | 36 | 4.3416 | 50.8519 | 2.8 | 20 | 20 | 20 | 12.9 | 20 | 20 | 20 | 17 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 2.6 | 20 | 20 | 20
PTSUD | PTSUD 36 | 36 | 4.3517 | 50.8387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
QDEME | QDEME 36 | 36 | 4.3186 | 50.8401 | 0.4 | 20 | 20 | 20 | 5.9 | 20 | 20 | 20 | 17 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0.4 | 20 | 20 | 20
QUEVA | QUEVA 70 | 70 | 3.6649 | 50.5145 | 1.5 | 3 | 4.8 | 7.2 | 0.8 | 6.5 | 7.9 | 10.5 | 1.4 | 26.8 | 34.7 | 48 | 1.2 | 6 | 9.3 | 15.9 | 0.8 | 2.9 | 4.8 | 7.2
RELEG | RELEG 36 | 36 | 4.2872 | 50.8933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RHODE | RHODE150 | 150 | 4.3553 | 50.7487 | 3.2 | 4.4 | 5.4 | 10 | 4.8 | 16.9 | 26.3 | 68.3 | 11.2 | 29 | 35.2 | 56.2 | 5.3 | 11.8 | 29.5 | 123.9 | 3.2 | 4.1 | 4.6 | 6.1
RIJKE | RIJKE 70 | 70 | 4.7453 | 51.3318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RIJKE | RIJKE150 | 150 | 4.7453 | 51.3318 | 4.3 | 40.5 | 111.1 | 175 | 4.1 | 8.7 | 14.3 | 46.6 | 7.2 | 15.5 | 19.9 | 36.4 | 5.6 | 17.2 | 35.6 | 98.7 | 4.1 | 8.7 | 14.3 | 46.6
RIMIE | RIMIE 70 | 70 | 5.471 | 50.5404 | 4.6 | 20.4 | 35.1 | 50 | 5.1 | 10 | 13.9 | 25.9 | 9.3 | 31 | 45.2 | 50 | 7.9 | 22.3 | 33.2 | 50 | 5.1 | 10 | 13.9 | 25.9
RIMIE | RIMIE220 | 220 | 5.471 | 50.5404 | 12.1 | 33 | 50.3 | 122.4 | 18.8 | 38.4 | 78.5 | 175 | 36.4 | 175 | 175 | 175 | 27.7 | 175 | 175 | 175 | 12 | 23 | 27.7 | 39.7
RIMIE | RIMIE380 | 380 | 5.471 | 50.5404 | 36.3 | 67 | 130.8 | 300 | 25.5 | 225.8 | 300 | 300 | 225.2 | 300 | 300 | 300 | 27.2 | 170.2 | 300 | 300 | 25.5 | 60.7 | 118 | 300
RINGV | RINGV150 | 150 | 3.7272 | 51.1067 | 7.6 | 100.2 | 161.6 | 175 | 35.3 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 91.5 | 175 | 175 | 175 | 5.9 | 9.1 | 11.8 | 25.2
RODEN | RODEN150 | 150 | 3.7753 | 51.1328 | 10.4 | 102 | 167.1 | 300 | 35.3 | 300 | 300 | 300 | 246.9 | 300 | 300 | 300 | 91.5 | 256.3 | 300 | 300 | 10.4 | 43.9 | 58 | 128.7
ROEVG | ROEVG 36 | 36 | 3.748 | 51.1084 | 7.6 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 5.9 | 9.4 | 12.4 | 20
ROMSE | ROMSE 70 | 70 | 5.6606 | 50.6138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ROMSE | ROMSE220 | 220 | 5.6606 | 50.6138 | 14.7 | 27.3 | 42.5 | 87.4 | 3.6 | 25 | 71.9 | 175 | 28.6 | 160.4 | 175 | 175 | 9.9 | 175 | 175 | 175 | 3.6 | 19.3 | 23 | 33.3
ROSIE | ROSIE 36 | 36 | 4.5304 | 50.7401 | 0.8 | 20 | 20 | 20 | 1 | 20 | 20 | 20 | 7.5 | 20 | 20 | 20 | 1.3 | 20 | 20 | 20 | 0.8 | 11.2 | 20 | 20
RUIEN | RUIEN 70 | 70 | 3.4874 | 50.7818 | 4.1 | 28.3 | 60 | 60 | 15.2 | 31.4 | 60 | 60 | 32.9 | 60 | 60 | 60 | 17.5 | 46.4 | 60 | 60 | 4.1 | 21.3 | 30 | 60
RUIEN | RUIEN150 | 150 | 3.4874 | 50.7818 | 14.2 | 27.8 | 113.2 | 175 | 14.9 | 30.6 | 111.1 | 175 | 32 | 175 | 175 | 175 | 17.1 | 45.2 | 108.2 | 175 | 14.2 | 25.7 | 41.7 | 116.2
SAIVE | SAIVE 70 | 70 | 5.2361 | 50.6678 | 1.4 | 4 | 11.1 | 43.4 | 1 | 13.9 | 28.4 | 50 | 1 | 50 | 50 | 50 | 1.2 | 15.8 | 29.8 | 50 | 1 | 4 | 13.1 | 31.3
SAMAN | SAMAN 36 | 36 | 3.7555 | 51.0513 | 2.3 | 20 | 20 | 20 | 1.1 | 20 | 20 | 20 | 14.6 | 20 | 20 | 20 | 3 | 20 | 20 | 20 | 1.1 | 4.4 | 8.3 | 16.6
SART | SART 220 | 220 | 5.5598 | 50.59 | 8.8 | 26.7 | 36.7 | 74.9 | 7.3 | 27.6 | 64.6 | 175 | 31.9 | 175 | 175 | 175 | 20.1 | 175 | 175 | 175 | 6.9 | 19.9 | 23.6 | 32.6
SART | SART 70 | 70 | 5.5598 | 50.59 | 2.8 | 28.8 | 38.9 | 50 | 7 | 14.3 | 25 | 50 | 13.7 | 50 | 50 | 50 | 10.3 | 50 | 50 | 50 | 6.8 | 14.3 | 25 | 35.5
SAUVE | SAUVE 70 | 70 | 4.7053 | 50.5776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SCARB | SCARB 36 | 36 | 4.3799 | 50.8818 | 8.7 | 11.6 | 12.9 | 16.5 | 31.8 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 44.2 | 60 | 60 | 60 | 8.7 | 11.2 | 12.2 | 14.7
SCARB | SCARB150 | 150 | 4.3799 | 50.8818 | 8.7 | 11.6 | 12.9 | 16.5 | 31.8 | 175 | 175 | 175 | 72.9 | 175 | 175 | 175 | 44.2 | 150.7 | 175 | 175 | 8.7 | 11.2 | 12.2 | 14.7
SCHED | SCHED 70 | 70 | 4.3393 | 51.1238 | 2.8 | 12.9 | 16.5 | 34.4 | 5.7 | 23.9 | 28 | 36.2 | 21.9 | 49.6 | 60 | 60 | 5.4 | 39.1 | 52.3 | 60 | 2.9 | 11.8 | 15.1 | 25.6
SCHEL | SCHEL 70 | 70 | 4.3124 | 51.1233 | 2.7 | 12.7 | 16.4 | 34.3 | 5.4 | 24.4 | 28.6 | 36.9 | 24.1 | 50 | 50 | 50 | 5.1 | 39.4 | 50 | 50 | 2.8 | 11.7 | 15 | 25.2
SCHEL | SCHEL150 | 150 | 4.3124 | 51.1233 | 6.3 | 12.3 | 15.7 | 32.6 | 15.1 | 20.6 | 24.3 | 31.9 | 36.5 | 117.3 | 157.1 | 175 | 18.6 | 36 | 50.3 | 85.4 | 6.3 | 11.5 | 14.4 | 24.1
SCHOL | SCHOL 36 | 36 | 4.3215 | 50.858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SDALE | SDALE150 | 150 | 3.3835 | 50.8917 | 4.7 | 32.3 | 111.9 | 175 | 20.7 | 74.6 | 174.3 | 175 | 54 | 175 | 175 | 175 | 27.2 | 98.7 | 175 | 175 | 4.1 | 6.9 | 10.5 | 32.9
SDEWE | SDEWE 36 | 36 | 3.6777 | 51.0187 | 0.5 | 17.3 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0.5 | 4.8 | 13.5 | 20
SEILL | SEILL 70 | 70 | 5.1063 | 50.5019 | 1.3 | 2.5 | 5.7 | 25.2 | 0.9 | 4.3 | 25.9 | 50 | 1.5 | 6 | 26.8 | 50 | 1.1 | 3.4 | 5.8 | 25.4 | 0.9 | 1.9 | 2.9 | 6.2
SENEF | SENEF 70 | 70 | 4.252 | 50.5267 | 1.9 | 11.6 | 20.6 | 50 | 5.8 | 12 | 17.2 | 33.9 | 17.5 | 50 | 50 | 50 | 8.1 | 14 | 21.5 | 50 | 1.1 | 11.2 | 17.2 | 30.5
SERAI | SERAI220 | 220 | 5.5229 | 50.6141 | 6.6 | 26.3 | 36 | 71.4 | 11 | 32.3 | 74.1 | 175 | 34.6 | 175 | 175 | 175 | 26.3 | 175 | 175 | 175 | 6.6 | 19.7 | 23.4 | 31.7
SIDAL | SIDAL150 | 150 | 4.4764 | 51.0823 | 3.3 | 5.8 | 11.4 | 17.8 | 9.3 | 26.2 | 31.2 | 40.6 | 24 | 45.9 | 58.3 | 85.7 | 10.3 | 32.9 | 55.7 | 83.2 | 3.3 | 5.1 | 7.9 | 13.6
SJOB | SJOB 70 | 70 | 4.5721 | 51.3023 | 5.2 | 50 | 50 | 50 | 1.1 | 18.3 | 32.1 | 50 | 1.1 | 24.6 | 32 | 50 | 2.3 | 37.1 | 50 | 50 | 1.1 | 18.3 | 32.1 | 50
SLAAN | SLAAN 36 | 36 | 4.3432 | 51.2506 | 4.2 | 4.9 | 5.2 | 6 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 4.2 | 4.9 | 5.1 | 5.8
SLAAN | SLAAN150 | 150 | 4.3432 | 51.2506 | 4.2 | 4.9 | 5.2 | 6 | 101.4 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 116.1 | 175 | 175 | 175 | 4.2 | 4.9 | 5.1 | 5.8
SLYKE | SLYKE 36 | 36 | 2.9529 | 51.2234 | 9.7 | 47.4 | 60 | 60 | 3 | 30.1 | 46.7 | 60 | 7.3 | 60 | 60 | 60 | 3.7 | 26.1 | 49.8 | 60 | 1.1 | 1.4 | 1.6 | 2
SLYKE | SLYKE150 | 150 | 2.9529 | 51.2234 | 13.9 | 47.4 | 85.3 | 175 | 3 | 30.1 | 46.7 | 67.6 | 7.3 | 132.3 | 163.2 | 175 | 3.7 | 26.1 | 49.8 | 93.9 | 3 | 29.6 | 46.1 | 67.6
SMARD | SMARD220 | 220 | 5.5143 | 49.5513 | 18.4 | 31.6 | 47.4 | 90.6 | 23.1 | 51 | 83.7 | 175 | 29.7 | 97.5 | 159.2 | 175 | 37.2 | 101.9 | 175 | 175 | 18.4 | 31.4 | 46.1 | 86.1
SOIGN | SOIGN 70 | 70 | 4.0882 | 50.572 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SOLRE | SOLRE 70 | 70 | 4.2536 | 50.2127 | 2.4 | 16.8 | 24.3 | 42.5 | 0.4 | 0.7 | 1.2 | 9.8 | 0.5 | 10.2 | 23 | 49.6 | 0.5 | 0.7 | 0.8 | 1.3 | 0.4 | 0.7 | 1.2 | 9.8
SOY | SOY 70 | 70 | 5.516 | 50.2896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
STALE | STALE150 | 150 | 5.5117 | 50.9924 | 7.8 | 28.5 | 35.9 | 73 | 50.6 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 82.1 | 175 | 175 | 175 | 7.8 | 21.8 | 34.2 | 69
STBAV | STBAV 70 | 70 | 3.3973 | 50.9105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
STBAV | STBAV150 | 150 | 3.3973 | 50.9105 | 10 | 31.5 | 109.3 | 175 | 21.2 | 75.4 | 175 | 175 | 55.3 | 175 | 175 | 175 | 27.9 | 90.2 | 175 | 175 | 4.3 | 7.4 | 11.2 | 35.1
STEMB | STEMB 70 | 70 | 5.8893 | 50.5979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
STENE | STENE 36 | 36 | 2.945 | 51.2145 | 6.7 | 20 | 20 | 20 | 3 | 20 | 20 | 20 | 7.3 | 20 | 20 | 20 | 3.7 | 20 | 20 | 20 | 0.2 | 1.4 | 1.5 | 2
STEVN | STEVN220 | 220 | 3.1848 | 51.3133 | 58.9 | 175 | 175 | 175 | 22.6 | 46.7 | 103.7 | 175 | 39.4 | 175 | 175 | 175 | 23.1 | 43.9 | 60.6 | 140.6 | 22.6 | 46.7 | 103.7 | 175
STEVN | STEVN380 | 380 | 3.1848 | 51.3133 | 58.9 | 300 | 300 | 300 | 22.6 | 46.7 | 103.7 | 300 | 39.4 | 300 | 300 | 300 | 23.1 | 43.9 | 60.6 | 140.7 | 22.6 | 46.7 | 103.7 | 300
STHUI | STHUI 70 | 70 | 5.4786 | 51.2374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
STRUI | STRUI 70 | 70 | 5.1979 | 50.8105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SVITH | SVITH 70 | 70 | 6.1356 | 50.2804 | 1.3 | 38 | 48.4 | 50 | 0.4 | 0.7 | 1.4 | 14.7 | 0.7 | 6.5 | 17 | 35.2 | 0.5 | 0.7 | 0.9 | 1.6 | 0.4 | 0.7 | 1.4 | 14.7
TABAK | TABAK 70 | 70 | 4.4098 | 51.2139 | 5.7 | 35.5 | 43 | 50 | 8.1 | 22.7 | 39 | 50 | 11.9 | 22 | 28.9 | 50 | 13.3 | 34.8 | 50 | 50 | 5.4 | 15.6 | 38.7 | 49.9
TERGN | TERGN150 | 150 | 4.5679 | 50.4368 | 4.5 | 18.8 | 28.8 | 54.6 | 5.3 | 14.7 | 79.5 | 203.3 | 22.3 | 294.4 | 300 | 300 | 13.4 | 90.6 | 184.1 | 300 | 4.5 | 11.7 | 22.1 | 38.3
TERGN | TERGN380 | 380 | 4.5679 | 50.4368 | 18.8 | 69.8 | 178.5 | 300 | 18.4 | 30.4 | 54.5 | 300 | 37.2 | 113.5 | 187.2 | 300 | 31.3 | 300 | 300 | 300 | 18.4 | 30.4 | 54.5 | 300
TERTR | TERTR 30 | 30 | 3.7964 | 50.4801 | 3.7 | 20 | 20 | 20 | 8 | 20 | 20 | 20 | 10.3 | 19.3 | 20 | 20 | 17.5 | 20 | 20 | 20 | 3.1 | 15.3 | 20 | 20
THYCH | THYCH 70 | 70 | 4.4418 | 50.2801 | 2.9 | 11.5 | 24.2 | 39.1 | 0.7 | 7.4 | 18.1 | 49.7 | 1.2 | 25.7 | 41.2 | 50 | 0.8 | 1.5 | 2.8 | 18.9 | 0.7 | 7.4 | 18.1 | 32.3
TIELT | TIELT150 | 150 | 3.34 | 50.9793 | 4.8 | 37.1 | 115.5 | 154.9 | 14.7 | 30.9 | 46.4 | 114.1 | 38.3 | 175 | 175 | 175 | 18.2 | 37.1 | 47.1 | 74.2 | 4.8 | 30.9 | 46.4 | 114.1
TIENE | TIENE 70 | 70 | 4.9264 | 50.8148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TIP | TIP 70 | 70 | 5.1615 | 51.0628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TISLT | TISLT 70 | 70 | 4.3564 | 51.025 | 0.8 | 2.4 | 12.4 | 19.3 | 10.9 | 50 | 50 | 50 | 36.4 | 50 | 50 | 50 | 20.7 | 48.4 | 50 | 50 | 0.8 | 1.4 | 2.7 | 8.8
TONGE | TONGE 70 | 70 | 5.4351 | 50.7751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TORHO | TORHO 36 | 36 | 3.1059 | 51.0758 | 0.4 | 17.6 | 20 | 20 | 0 | 20 | 20 | 20 | 0 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0 | 15.3 | 18.7 | 20
TOURN | TOURN 70 | 70 | 3.3803 | 50.6224 | 2.9 | 25.3 | 46.7 | 50 | 15.3 | 31.1 | 50 | 50 | 33 | 50 | 50 | 50 | 20.1 | 50 | 50 | 50 | 2.9 | 19.8 | 40.6 | 50
TRIVI | TRIVI150 | 150 | 4.1378 | 50.4535 | 8.4 | 21.7 | 30.7 | 52.9 | 13.1 | 49.8 | 69.5 | 108.7 | 27.8 | 175 | 175 | 175 | 32.1 | 67.7 | 143.7 | 175 | 8.4 | 19.4 | 28 | 45.1
TURNH | TURNH 70 | 70 | 4.9335 | 51.312 | 1 | 2.8 | 25.2 | 50 | 1.5 | 7.8 | 13.1 | 37.5 | 1.8 | 17.4 | 21.9 | 36.7 | 2.5 | 19.1 | 35 | 50 | 1 | 2.8 | 13.1 | 37.5
TURON | TURON 70 | 70 | 5.8199 | 50.5135 | 15.5 | 28.8 | 37.7 | 48.5 | 5.4 | 20.8 | 49.9 | 50 | 9.3 | 21.5 | 50 | 50 | 25 | 50 | 50 | 50 | 4 | 19.7 | 24.4 | 31.3
VANYK | VANYK380 | 380 | 5.7739 | 51.1213 | 98.6 | 300 | 300 | 300 | 211.3 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 98.6 | 300 | 300 | 300
VERBR | VERBR150 | 150 | 4.4224 | 50.9409 | 9.5 | 11.5 | 12.6 | 15.2 | 31.8 | 289.8 | 300 | 300 | 72.9 | 300 | 300 | 300 | 44.2 | 150.7 | 300 | 300 | 9.5 | 11.3 | 12.2 | 14.2
VHAIN | VHAIN150 | 150 | 4.0723 | 50.469 | 5.1 | 22.4 | 33.3 | 56.7 | 17.1 | 41.1 | 51 | 67.3 | 35.1 | 158.7 | 175 | 175 | 26.1 | 68.2 | 85.4 | 120.4 | 5.1 | 19.5 | 26.6 | 41.7
VILLE | VILLE 70 | 70 | 5.6626 | 49.9759 | 1.4 | 5 | 7.5 | 20.2 | 1.3 | 4.3 | 7.2 | 28.1 | 2.2 | 39 | 60 | 60 | 1.5 | 6.1 | 24.9 | 60 | 1.3 | 4.3 | 7.2 | 23.7
VILLE | VILLE220 | 220 | 5.6626 | 49.9759 | 7.5 | 37.8 | 50.2 | 83.5 | 4.6 | 20.2 | 60.9 | 141.9 | 14.8 | 175 | 175 | 175 | 6.8 | 65.6 | 155.4 | 175 | 4.6 | 20.2 | 49.5 | 81.4
VISEM | VISEM 70 | 70 | 5.5607 | 49.6963 | 0.9 | 2.8 | 3.6 | 6.7 | 1 | 3.3 | 4.9 | 14.8 | 2.7 | 5.1 | 6.3 | 10.5 | 2.7 | 9.8 | 17.1 | 50 | 0.9 | 2.7 | 4.9 | 14.8
VTAIR | VTAIR 36 | 36 | 4.3805 | 50.8635 | 8.7 | 11.6 | 12.9 | 16.6 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 8.7 | 11.2 | 12.2 | 14.7
WAARS | WAARS 36 | 36 | 3.6171 | 51.1534 | 0.7 | 12.1 | 13.6 | 16 | 0.6 | 17.2 | 18.4 | 20 | 1 | 20 | 20 | 20 | 15.5 | 20 | 20 | 20 | 0.6 | 10.3 | 12.5 | 15
WARNA | WARNA 70 | 70 | 4.84 | 50.3211 | 1.4 | 3.9 | 6.2 | 22.3 | 0.4 | 0.4 | 0.5 | 0.6 | 0.5 | 1.2 | 1.6 | 2.3 | 0.4 | 0.5 | 0.6 | 0.9 | 0.4 | 0.4 | 0.5 | 0.6
WAYS | WAYS 36 | 36 | 4.4713 | 50.6134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WETTE | WETTE 36 | 36 | 3.8826 | 51.0106 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WEZEM | WEZEM 36 | 36 | 4.4856 | 50.8552 | 4.9 | 11.4 | 12.7 | 16.1 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0.7 | 10.7 | 11.7 | 13.8
WICHE | WICHE 36 | 36 | 3.9913 | 51.0015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WIJGM | WIJGM150 | 150 | 4.6922 | 50.939 | 5.2 | 9.5 | 11 | 14 | 22.4 | 161.4 | 175 | 175 | 59.9 | 175 | 175 | 175 | 38.8 | 132.3 | 175 | 175 | 5 | 9 | 10.5 | 13.5
WILRI | WILRI 70 | 70 | 4.3761 | 51.1705 | 2.9 | 10.4 | 12.5 | 18.7 | 5.6 | 22.4 | 24.9 | 31.2 | 23 | 50 | 50 | 50 | 5.3 | 36.7 | 46.4 | 50 | 2.9 | 10.2 | 11.9 | 16.6
WILSE | WILSE 70 | 70 | 4.7081 | 50.9025 | 3.5 | 8.7 | 11.7 | 16 | 34.5 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 3.5 | 5.6 | 8.6 | 13.5
WILSE | WILSE150 | 150 | 4.7081 | 50.9025 | 2.8 | 7.6 | 12.4 | 16.7 | 34.6 | 175 | 175 | 175 | 129.3 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 2.8 | 4.5 | 7 | 13.3
WIRTZ | WIRTZ 36 | 36 | 4.3763 | 50.8394 | 4.3 | 20 | 20 | 20 | 5.8 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 4 | 20 | 20 | 20
WOLUW | WOLUW 36 | 36 | 4.4603 | 50.8502 | 4.9 | 11.4 | 12.7 | 16.3 | 31.8 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 44.2 | 60 | 60 | 60 | 1 | 10.8 | 11.8 | 14.1
WOLUW | WOLUW150 | 150 | 4.4603 | 50.8502 | 5.4 | 11.4 | 12.7 | 16.2 | 31.8 | 175 | 175 | 175 | 72.9 | 175 | 175 | 175 | 44.2 | 150.7 | 175 | 175 | 5.4 | 10.7 | 11.8 | 14.1
WORTG | WORTG 70 | 70 | 3.4865 | 50.8628 | 1.5 | 24.2 | 45.1 | 50 | 1.5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 38.4 | 50 | 50 | 50 | 1.4 | 3.3 | 8.9 | 24
WORTG | WORTG150 | 150 | 3.4865 | 50.8628 | 15.3 | 28.5 | 101.6 | 175 | 23.4 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 38.1 | 175 | 175 | 175 | 4.6 | 12.4 | 18.7 | 58.7
WVLGM | WVLGM150 | 150 | 3.147 | 50.7995 | 9.9 | 34.5 | 76.4 | 108 | 28.6 | 171.6 | 175 | 175 | 120 | 175 | 175 | 175 | 88.9 | 175 | 175 | 175 | 2.7 | 31 | 53.2 | 78.7
ZANDV | ZANDV150 | 150 | 4.2481 | 51.3695 | 7.8 | 177.7 | 234.5 | 298.8 | 62.6 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 85.8 | 300 | 300 | 300 | 7.8 | 156.5 | 190.9 | 261
ZANDV | ZANDV380 | 380 | 4.2481 | 51.3695 | 94.7 | 173.3 | 218.6 | 300 | 140 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 203.2 | 300 | 300 | 300 | 92.8 | 169.4 | 205.2 | 300
ZAVEN | ZAVEN 36 | 36 | 4.4776 | 50.8861 | 4.9 | 11.4 | 12.7 | 16.2 | 1.9 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 2.7 | 20 | 20 | 20 | 1.2 | 10.7 | 11.7 | 13.8
ZECHP | ZECHP 36 | 36 | 3.2248 | 51.3493 | 0 | 7.1 | 18.7 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0 | 0 | 0 | 4.3
ZEDEL | ZEDEL 36 | 36 | 3.1558 | 51.1309 | 4.1 | 12.5 | 19.6 | 59.1 | 0 | 60 | 60 | 60 | 0 | 60 | 60 | 60 | 30.7 | 60 | 60 | 60 | 0 | 18.7 | 26.9 | 45
ZEEBR | ZEEBR 36 | 36 | 3.1926 | 51.3186 | 0.2 | 5.9 | 17.5 | 32.5 | 8.2 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 11.4 | 60 | 60 | 60 | 0.2 | 0.2 | 0.2 | 3.3
ZEEBR | ZEEBR150 | 150 | 3.1926 | 51.3186 | 9.2 | 103.6 | 175 | 175 | 8.2 | 175 | 175 | 175 | 79.7 | 175 | 175 | 175 | 11.4 | 175 | 175 | 175 | 8.2 | 105.1 | 175 | 175
ZELEI | ZELEI 36 | 36 | 4.0505 | 51.078 | 1.1 | 9.4 | 60 | 60 | 11 | 13.3 | 14.6 | 18.1 | 20.6 | 60 | 60 | 60 | 12.7 | 19.2 | 23.5 | 32.8 | 1.1 | 3.1 | 14.6 | 18.1
ZOGLI | ZOGLI 30 | 30 | 3.87 | 50.4829 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ZONHO | ZONHO 70 | 70 | 5.3479 | 50.9908 | 3.5 | 16.3 | 23.7 | 35 | 6 | 17.7 | 50 | 50 | 50 | 50 | 50 | 50 | 9.1 | 50 | 50 | 50 | 1.3 | 17.7 | 32.9 | 50
ZOTGM | ZOTGM 70 | 70 | 3.8163 | 50.8795 | 1.8 | 15.7 | 21.5 | 34.4 | 1.3 | 1.8 | 2.5 | 6.4 | 2.4 | 15.2 | 29.1 | 50 | 1.7 | 3.2 | 5.5 | 12 | 1.2 | 1.8 | 2.4 | 3
ZUDOK | ZUDOK 36 | 36 | 3.2376 | 51.3066 | 0 | 3.5 | 4.7 | 7.1 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0 | 0 | 0 | 3.2
ZUREN | ZUREN 70 | 70 | 4.4364 | 51.2046 | 5.4 | 35.6 | 43.3 | 50 | 8.1 | 20.8 | 36.3 | 50 | 11.8 | 22.4 | 29.3 | 50 | 13.4 | 41.2 | 50 | 50 | 5.4 | 15 | 36.3 | 50
ZUREN | ZUREN150 | 150 | 4.4364 | 51.2046 | 4.7 | 44.3 | 90.3 | 175 | 9 | 25.8 | 50.3 | 175 | 17.8 | 44.3 | 66.1 | 132.1 | 15.3 | 47.2 | 97.6 | 175 | 3.9 | 13.4 | 50.3 | 116.8
ZWIJN | ZWIJN 36 | 36 | 4.3284 | 51.2313 | 4.2 | 4.9 | 5.2 | 6 | 4.5 | 6.8 | 8.7 | 19.8 | 9.6 | 60 | 60 | 60 | 8.3 | 60 | 60 | 60 | 4.2 | 4.9 | 5.1 | 5.8
ZWIJN | ZWIJN150 | 150 | 4.3284 | 51.2313 | 4.2 | 4.9 | 5.2 | 6 | 4.5 | 6.8 | 8.7 | 19.8 | 9.6 | 95.6 | 175 | 175 | 8.3 | 71.4 | 145.5 | 175 | 4.2 | 4.9 | 5.1 | 5.8

## 2031
Site | Substation | Voltage (kV) | Longitude Easting (deg) | Latitude Northing (deg) | Hosting Capacity (MW)
[5 empty] | Load_0%_flex | Load_5%_flex | Load_10%_flex | Load_20%_flex | Prod_0%_flex | Prod_5%_flex | Prod_10%_flex | Prod_20%_flex | PV_0%_flex | PV_5%_flex | PV_10%_flex | PV_20%_flex | Wind_0%_flex | Wind_5%_flex | Wind_10%_flex | Wind_20%_flex | Battery_0%_flex | Battery_5%_flex | Battery_10%_flex | Battery_20%_flex
AALST | AALST 70 | 70 | 4.0504 | 50.9313 | 1.9 | 15 | 21.3 | 30.9 | 7 | 32.8 | 43.4 | 50 | 46.2 | 50 | 50 | 50 | 16.2 | 39.3 | 50 | 50 | 1.7 | 2 | 2.2 | 2.6
AALTR | AALTR 36 | 36 | 3.4527 | 51.1018 | 21 | 60 | 60 | 60 | 8.2 | 60 | 60 | 60 | 13.2 | 60 | 60 | 60 | 37.3 | 60 | 60 | 60 | 7.3 | 60 | 60 | 60
AARSC | AARSC 70 | 70 | 4.841 | 50.986 | 1.4 | 2.4 | 5.4 | 16.1 | 1.8 | 50 | 50 | 50 | 2.8 | 50 | 50 | 50 | 6.9 | 50 | 50 | 50 | 1.4 | 2.4 | 5.2 | 14.1
ABEE | ABEE 70 | 70 | 5.3713 | 50.4943 | 0.7 | 2.2 | 6.3 | 35 | 0.7 | 18 | 33.7 | 50 | 1.2 | 50 | 50 | 50 | 1 | 22.1 | 32.5 | 50 | 0.7 | 1.6 | 2.4 | 14.3
ACHEN | ACHEN 70 | 70 | 5.0554 | 50.2605 | 3.8 | 20.5 | 60 | 60 | 1.9 | 9.2 | 48.7 | 60 | 5.7 | 42.6 | 60 | 60 | 2.3 | 7.2 | 15.6 | 60 | 1.9 | 9.2 | 48.7 | 60
ACHEN | ACHEN380 | 380 | 5.0554 | 50.2605 | 52.6 | 300 | 300 | 300 | 68.2 | 162.6 | 272.6 | 300 | 157 | 300 | 300 | 300 | 142.9 | 300 | 300 | 300 | 52.6 | 162.6 | 272.6 | 300
AIRLI | AIRLI 30 | 30 | 3.8557 | 50.4778 | 1.3 | 4.6 | 10.9 | 15 | 8 | 22.4 | 37.4 | 47.4 | 10.3 | 19.4 | 27.1 | 60 | 17.6 | 37.2 | 60 | 60 | 1.1 | 4.2 | 9.6 | 13.2
ALKEN | ALKEN 70 | 70 | 5.2922 | 50.8753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AMERC | AMERC150 | 150 | 4.3946 | 50.4314 | 12.8 | 30.2 | 40 | 64.9 | 18.1 | 99.2 | 131.4 | 175 | 32.3 | 175 | 175 | 175 | 42.3 | 95 | 175 | 175 | 12.8 | 26.2 | 34.9 | 55.1
AMPSI | AMPSI 70 | 70 | 5.2982 | 50.5342 | 1.5 | 3.6 | 14.6 | 35.1 | 1.2 | 36.3 | 50 | 50 | 2 | 50 | 50 | 50 | 1.6 | 39.3 | 50 | 50 | 1.2 | 2.2 | 3.3 | 18.6
ANDUM | ANDUM150 | 150 | 5.4857 | 50.9403 | 9.3 | 47.3 | 150.7 | 175 | 14.2 | 175 | 175 | 175 | 43.2 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 9.2 | 46.8 | 132.5 | 175
ANDUM | ANDUM380 | 380 | 5.4857 | 50.9403 | 146.4 | 300 | 300 | 300 | 22.1 | 213.7 | 300 | 300 | 149.3 | 300 | 300 | 300 | 69.1 | 300 | 300 | 300 | 22.1 | 213.7 | 300 | 300
ANGLE | ANGLE 70 | 70 | 5.582 | 50.6184 | 12.3 | 29.6 | 39.7 | 50 | 1.6 | 16.8 | 35.5 | 50 | 2.6 | 50 | 50 | 50 | 21.3 | 50 | 50 | 50 | 1.6 | 16.8 | 25 | 34.3
ANS | ANS 150 | 150 | 5.5233 | 50.655 | 4.2 | 27.1 | 38 | 71.5 | 4.4 | 36.8 | 67.2 | 175 | 22.3 | 43 | 63.2 | 175 | 11.6 | 98.2 | 161.2 | 175 | 4.2 | 20 | 27.9 | 39.8
ANS | ANS 70 | 70 | 5.5233 | 50.655 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ANTHI | ANTHI 70 | 70 | 5.5301 | 50.4727 | 0.7 | 1.4 | 3 | 31.5 | 0.7 | 5.7 | 11.6 | 42.6 | 1.2 | 50 | 50 | 50 | 1 | 30.4 | 50 | 50 | 0.7 | 1.3 | 2.9 | 27.3
ANTOI | ANTOI150 | 150 | 3.4428 | 50.5716 | 1.9 | 23.4 | 42.7 | 77.7 | 24.2 | 175 | 175 | 175 | 116.2 | 175 | 175 | 175 | 55.8 | 175 | 175 | 175 | 1.7 | 12.5 | 31.2 | 69.9
ARLON | ARLON 70 | 70 | 5.8178 | 49.6711 | 1 | 1.7 | 2.2 | 5 | 1.2 | 2.3 | 3.4 | 13.4 | 2.2 | 4.2 | 5.1 | 8.1 | 1.7 | 5.4 | 9.9 | 50 | 1 | 1.7 | 2.2 | 5
AUBAN | AUBAN 70 | 70 | 5.7943 | 49.5668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AUBAN | AUBAN220 | 220 | 5.7943 | 49.5668 | 18.4 | 31.5 | 47.2 | 89.2 | 23.1 | 54.5 | 107.8 | 175 | 29.7 | 97.4 | 159.2 | 175 | 37.2 | 100.7 | 175 | 175 | 18.4 | 31.4 | 44.7 | 84.9
AUBAN | AUBAN380 | 380 | 5.7943 | 49.5668 | 21.1 | 32.2 | 42.5 | 80.9 | 5.7 | 37.8 | 82 | 163.1 | 15 | 100.5 | 190.5 | 300 | 8.4 | 110.3 | 182.3 | 300 | 5.7 | 32.1 | 42.5 | 80.8
AUVEL | AUVEL 30 | 30 | 4.6212 | 50.4556 | 0.6 | 1.1 | 3 | 13.5 | 7 | 40.7 | 60 | 60 | 60 | 60 | 60 | 60 | 13.5 | 60 | 60 | 60 | 0.6 | 1.1 | 3 | 13.5
AUVEL | AUVEL 70 | 70 | 4.6212 | 50.4556 | 1.4 | 2.7 | 11.5 | 31.8 | 0.6 | 0.9 | 1.5 | 12.7 | 1 | 10.8 | 21.6 | 50 | 0.6 | 0.9 | 1.1 | 1.7 | 0.6 | 0.9 | 1.5 | 12.1
AVERN | AVERN150 | 150 | 5.0602 | 50.7132 | 3.5 | 38.8 | 54.2 | 107.5 | 3 | 23.8 | 55.3 | 140.5 | 5.7 | 175 | 175 | 175 | 3.7 | 8 | 18.1 | 148.2 | 3 | 20.1 | 38.1 | 54.9
AVLGM | AVLGM380 | 380 | 3.469 | 50.7824 | 102.9 | 300 | 300 | 300 | 133.3 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 152.7 | 300 | 300 | 300 | 102.9 | 231.7 | 300 | 300
AWIRS | AWIRS 70 | 70 | 5.4151 | 50.5846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AWIRS | AWIRS150 | 150 | 5.4151 | 50.5846 | 5.2 | 18.8 | 33.5 | 77.1 | 13.2 | 36.2 | 58.8 | 175 | 57.9 | 175 | 175 | 175 | 20.6 | 157.9 | 175 | 175 | 5.2 | 15.9 | 28.5 | 42.8
AWIRS | AWIRS220 | 220 | 5.4151 | 50.5846 | 9.3 | 31.5 | 44.1 | 90.4 | 16.4 | 32.8 | 59.1 | 175 | 28.4 | 175 | 175 | 175 | 29.2 | 175 | 175 | 175 | 12.9 | 23.5 | 27.4 | 38.2
BAASR | BAASR 70 | 70 | 4.1799 | 51.028 | 3.5 | 20.9 | 30.5 | 50 | 9.3 | 39 | 50 | 50 | 50 | 50 | 50 | 50 | 20.8 | 50 | 50 | 50 | 1.6 | 2 | 2.2 | 2.7
BAEKE | BAEKE150 | 150 | 3.7863 | 51.1291 | 36.5 | 300 | 300 | 300 | 17.1 | 128.8 | 210.3 | 300 | 174.5 | 300 | 300 | 300 | 27.9 | 237.3 | 300 | 300 | 17.1 | 44.8 | 59.7 | 133.8
BAEKE | BAEKE380 | 380 | 3.7863 | 51.1291 | 69.8 | 203.5 | 300 | 300 | 100.1 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 118.9 | 254.5 | 300 | 300 | 69.8 | 202.7 | 300 | 300
BAISY | BAISY 36 | 36 | 4.488 | 50.6527 | 2.5 | 12.9 | 29.3 | 60 | 1.9 | 17 | 32.4 | 60 | 4.1 | 60 | 60 | 60 | 2.3 | 21.2 | 60 | 60 | 1.9 | 10 | 18.6 | 51.3
BAISY | BAISY150 | 150 | 4.488 | 50.6527 | 5.3 | 13.1 | 34.7 | 145.1 | 4.8 | 15.1 | 22.5 | 61.2 | 7.5 | 26.1 | 31.6 | 50.5 | 5.6 | 12.8 | 28.6 | 121.6 | 4.8 | 12.5 | 22.5 | 61.2
BALEN | BALEN150 | 150 | 5.2222 | 51.2019 | 6.6 | 23.5 | 54.9 | 149.3 | 12 | 175 | 175 | 175 | 29.6 | 175 | 175 | 175 | 17.5 | 175 | 175 | 175 | 6.6 | 22.6 | 42 | 98.5
BASSW | BASSW 36 | 36 | 4.6284 | 50.7232 | 1.1 | 12.5 | 20 | 20 | 4.8 | 15.1 | 20 | 20 | 7.5 | 20 | 20 | 20 | 5.6 | 12.9 | 20 | 20 | 1.1 | 9.1 | 19.1 | 20
BAUDO | BAUDO 70 | 70 | 3.8261 | 50.4704 | 1.5 | 7.3 | 8.5 | 10.6 | 1.5 | 7.5 | 8.9 | 11.2 | 2.5 | 24 | 30.9 | 43.2 | 2.1 | 8.7 | 11.3 | 18 | 1.5 | 5.7 | 6.9 | 8.9
BAUDO | BAUDO150 | 150 | 3.8261 | 50.4704 | 9.9 | 28.7 | 38.8 | 60.7 | 7.9 | 20.3 | 33.3 | 44.1 | 10.2 | 19.2 | 26.7 | 71.7 | 17.2 | 36.5 | 60.6 | 88 | 7.9 | 20.3 | 25.6 | 34.6
BEAGA | BEAGA150 | 150 | 4.2973 | 50.862 | 12.9 | 25.1 | 38.3 | 122.5 | 13.6 | 70.6 | 175 | 175 | 43.3 | 118.3 | 175 | 175 | 24.9 | 175 | 175 | 175 | 3.3 | 23.2 | 35.3 | 122
BEERN | BEERN 36 | 36 | 3.2976 | 51.1275 | 0.2 | 4.8 | 10.7 | 14.4 | 0 | 9.6 | 19.8 | 20 | 0 | 0.4 | 0.8 | 12.7 | 0.6 | 20 | 20 | 20 | 0 | 0.3 | 0.6 | 2.9
BEERS | BEERS 70 | 70 | 4.8533 | 51.3263 | 1.3 | 8.2 | 49 | 60 | 1.3 | 5.4 | 10 | 31.9 | 2.7 | 10.3 | 14.5 | 26.6 | 2.3 | 15.7 | 22.2 | 54.5 | 1.3 | 3.7 | 10 | 31.9
BEERS | BEERS150 | 150 | 4.8533 | 51.3263 | 4.1 | 95.2 | 175 | 175 | 3.9 | 10 | 16.4 | 40.6 | 6.8 | 14.2 | 17.9 | 31.4 | 5.3 | 16.3 | 28.5 | 86.7 | 3.9 | 10 | 16.4 | 40.6
BEREN | BEREN 36 | 36 | 4.2839 | 51.3399 | 0.3 | 3.9 | 7.1 | 10.1 | 7.7 | 13.5 | 14.9 | 18.7 | 13.9 | 20 | 20 | 20 | 8.3 | 18.9 | 20 | 20 | 0.3 | 3.9 | 7.1 | 10.1
BERIN | BERIN150 | 150 | 5.2134 | 51.0668 | 10.1 | 19.1 | 24.2 | 50.3 | 16.6 | 175 | 175 | 175 | 103.5 | 175 | 175 | 175 | 22.1 | 175 | 175 | 175 | 9.7 | 18.8 | 23.5 | 43.1
BERNE | BERNE220 | 220 | 5.7372 | 50.7535 | 8.4 | 16.1 | 26 | 60.9 | 7.2 | 19.6 | 38.2 | 175 | 19.3 | 175 | 175 | 175 | 15 | 126.8 | 175 | 175 | 7 | 14.9 | 18.8 | 30.8
BEVER | BEVER 70 | 70 | 6.0387 | 50.439 | 1 | 1.5 | 2.5 | 16.6 | 0.6 | 0.9 | 1.5 | 3.3 | 0.9 | 2.8 | 4 | 9.1 | 0.6 | 0.9 | 1.1 | 1.7 | 0.6 | 0.9 | 1.5 | 3.3
BEVER | BEVER110 | 110 | 6.0387 | 50.439 | 5.8 | 36.7 | 50.2 | 61.3 | 1.2 | 2.3 | 3.5 | 21.5 | 2.1 | 26.4 | 45.8 | 93.1 | 1.3 | 2 | 2.7 | 4.6 | 1.2 | 2.3 | 3.5 | 21.5
BIERG | BIERG 36 | 36 | 4.5973 | 50.7056 | 0.7 | 15.8 | 20 | 20 | 4.8 | 15.1 | 20 | 20 | 7.5 | 20 | 20 | 20 | 5.6 | 12.9 | 20 | 20 | 0.7 | 7.5 | 14.3 | 20
BILZE | BILZE 70 | 70 | 5.5055 | 50.8765 | 1.2 | 13.1 | 43.3 | 50 | 6.9 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 7.4 | 50 | 50 | 50 | 1.2 | 9.4 | 37.7 | 50
BLTOR | BLTOR150 | 150 | 3.1927 | 51.2614 | 19.2 | 98 | 175 | 175 | 6.7 | 115.6 | 175 | 175 | 10.8 | 175 | 175 | 175 | 18.3 | 175 | 175 | 175 | 6.1 | 57.7 | 175 | 175
BOISD | BOISD 70 | 70 | 4.8087 | 50.3823 | 3.9 | 8 | 25 | 39.1 | 0.7 | 1.1 | 1.5 | 12.1 | 1.5 | 18 | 35.1 | 50 | 0.8 | 1.2 | 1.5 | 2.2 | 0.7 | 1.1 | 1.5 | 12.1
BOMAL | BOMAL 70 | 70 | 5.5145 | 50.3771 | 0.6 | 1.9 | 6.4 | 24.8 | 0.8 | 16.1 | 24 | 45.5 | 2.2 | 50 | 50 | 50 | 1.8 | 39.4 | 50 | 50 | 0.6 | 1.6 | 4.6 | 22.3
BONNE | BONNE 70 | 70 | 5.8271 | 49.7105 | 1.1 | 1.9 | 2.4 | 5.1 | 1.3 | 1.9 | 2.9 | 11.1 | 1.7 | 3.1 | 3.8 | 6.3 | 1.6 | 4.6 | 9 | 50 | 1.1 | 1.9 | 2.4 | 5.1
BORGL | BORGL 70 | 70 | 5.3377 | 50.7914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BORNM | BORNM 70 | 70 | 4.2676 | 51.0896 | 3.4 | 20.7 | 29.3 | 50 | 7.6 | 18.9 | 30.3 | 50 | 28.2 | 50 | 50 | 50 | 15.3 | 36 | 50 | 50 | 1.6 | 2 | 2.2 | 2.7
BOTAN | BOTAN 36 | 36 | 4.3635 | 50.8552 | 1.8 | 20 | 20 | 20 | 13.6 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 1.4 | 20 | 20 | 20
BRAIN | BRAIN150 | 150 | 4.367 | 50.6861 | 4.5 | 13.5 | 53.7 | 175 | 4.8 | 12.8 | 19.2 | 52.1 | 6.4 | 22.5 | 27.3 | 43.6 | 5.3 | 10.8 | 24.1 | 102.5 | 4.5 | 11.9 | 19.2 | 52.1
BRESS | BRESS150 | 150 | 5.6123 | 50.6486 | 18.4 | 27.4 | 36.2 | 73.8 | 6.1 | 25.2 | 61.8 | 175 | 9.1 | 20.9 | 45.8 | 166.7 | 24.3 | 175 | 175 | 175 | 3.9 | 17.5 | 23.2 | 29.8
BRUEG | BRUEG150 | 150 | 4.2317 | 50.881 | 12.9 | 25.3 | 38.6 | 123 | 13.7 | 69.1 | 272.9 | 300 | 43.3 | 118.3 | 300 | 300 | 24.9 | 300 | 300 | 300 | 12.6 | 17 | 20.5 | 30.1
BRUEG | BRUEG380 | 380 | 4.2317 | 50.881 | 48.2 | 265.7 | 300 | 300 | 128.9 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 147.4 | 300 | 300 | 300 | 45.7 | 131.7 | 286.1 | 300
BRUGG | BRUGG 36 | 36 | 3.1991 | 51.216 | 17.8 | 60 | 60 | 60 | 6.7 | 60 | 60 | 60 | 10.8 | 60 | 60 | 60 | 18.3 | 60 | 60 | 60 | 6 | 51 | 60 | 60
BRUGG | BRUGG150 | 150 | 3.1991 | 51.216 | 17.8 | 83.7 | 158.6 | 175 | 6.7 | 103 | 167.5 | 175 | 10.8 | 175 | 175 | 175 | 18.3 | 175 | 175 | 175 | 6 | 51 | 145 | 175
BRUME | BRUME220 | 220 | 5.843 | 50.3755 | 5.1 | 39.6 | 56.9 | 116.1 | 3 | 23.4 | 76.1 | 169.4 | 5 | 103.8 | 175 | 175 | 3.4 | 5.5 | 9.3 | 46.4 | 3 | 23.4 | 56.5 | 114.5
BRUME | BRUME380 | 380 | 5.843 | 50.3755 | 18.6 | 37.1 | 73.3 | 300 | 49 | 181.7 | 300 | 300 | 163 | 300 | 300 | 300 | 63.3 | 300 | 300 | 300 | 18.6 | 37 | 73.1 | 300
BRUNY | BRUNY 36 | 36 | 3.2412 | 51.2072 | 17.8 | 20 | 20 | 20 | 6.7 | 20 | 20 | 20 | 10.8 | 20 | 20 | 20 | 18.3 | 20 | 20 | 20 | 6 | 20 | 20 | 20
BRUST | BRUST 70 | 70 | 5.2213 | 50.8147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BRUZU | BRUZU 36 | 36 | 3.2224 | 51.1939 | 12.7 | 20 | 20 | 20 | 6.7 | 20 | 20 | 20 | 10.8 | 20 | 20 | 20 | 18.3 | 20 | 20 | 20 | 6 | 20 | 20 | 20
BUDA | BUDA 36 | 36 | 4.413 | 50.9064 | 4.7 | 10.7 | 13.7 | 18.6 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 4.7 | 6.4 | 8.5 | 15.7
BUIZI | BUIZI150 | 150 | 4.2577 | 50.749 | 4.2 | 8.2 | 19.6 | 175 | 4.9 | 25.3 | 103.3 | 175 | 38.1 | 80.4 | 128 | 175 | 6.7 | 73.3 | 175 | 175 | 4.2 | 7.7 | 14.6 | 27.6
BURCH | BURCH150 | 150 | 4.348 | 51.2103 | 5 | 121.5 | 161.9 | 175 | 9 | 164 | 175 | 175 | 22.4 | 125.4 | 175 | 175 | 15.3 | 47.4 | 98.5 | 175 | 3.9 | 13.4 | 58.3 | 127.1
BVREN | BVREN150 | 150 | 3.1268 | 50.9656 | 6.3 | 38.6 | 125.7 | 175 | 26.1 | 62.6 | 95.3 | 175 | 124.9 | 175 | 175 | 175 | 28.4 | 72.8 | 91.2 | 141.3 | 4.5 | 21.8 | 63.3 | 100.9
BWTON | BWTON150 | 150 | 2.9421 | 50.7707 | 3.1 | 31.6 | 81.3 | 100.1 | 25.2 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 94.5 | 175 | 175 | 175 | 2.3 | 34.6 | 63.1 | 76.6
CENTE | CENTE 36 | 36 | 4.3472 | 50.8942 | 0.8 | 12.4 | 14.3 | 19.1 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0.7 | 11.8 | 13.1 | 16.9
CHAMP | CHAMP 70 | 70 | 4.9038 | 50.4887 | 2.5 | 6 | 16.1 | 60 | 2.5 | 7.6 | 11.8 | 28.4 | 4.2 | 47.6 | 60 | 60 | 3 | 6.3 | 9.9 | 60 | 2.5 | 5.9 | 11.8 | 28.4
CHAMP | CHAMP380 | 380 | 4.9038 | 50.4887 | 24.9 | 70.6 | 137 | 300 | 29.1 | 213.3 | 300 | 300 | 123.8 | 300 | 300 | 300 | 37.6 | 236.6 | 300 | 300 | 24.8 | 63.6 | 115.3 | 300
CHASS | CHASS 70 | 70 | 4.5223 | 50.5303 | 4.5 | 18.5 | 26.1 | 43.1 | 0.3 | 0.4 | 0.5 | 0.7 | 0.5 | 1.1 | 1.4 | 2 | 0.4 | 0.6 | 0.7 | 0.9 | 0.3 | 0.4 | 0.5 | 0.7
CHIEV | CHIEV150 | 150 | 3.7514 | 50.5816 | 7.3 | 36.5 | 74.2 | 115.4 | 11.2 | 19 | 36.5 | 95.6 | 20.3 | 38 | 51.1 | 115.2 | 12.2 | 25.3 | 48.7 | 175 | 7.3 | 19 | 36.5 | 60.5
CHIEV | CHIEV380 | 380 | 3.7514 | 50.5816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CHINY | CHINY 70 | 70 | 5.3482 | 49.7148 | 0.4 | 0.7 | 1.1 | 7.7 | 0.4 | 0.6 | 0.8 | 2.8 | 0.5 | 1 | 1.3 | 1.9 | 0.5 | 2.7 | 5.3 | 15.6 | 0.4 | 0.6 | 0.8 | 2.8
CIERR | CIERR 70 | 70 | 5.9134 | 50.2496 | 1.4 | 27.8 | 48.6 | 50 | 1.1 | 1.5 | 1.8 | 3.2 | 1.5 | 3.4 | 4.4 | 6.5 | 1.3 | 1.9 | 2.2 | 3 | 1.1 | 1.5 | 1.8 | 3.2
CLANG | CLANG 36 | 36 | 3.7442 | 51.1148 | 7.6 | 60 | 60 | 60 | 1.4 | 60 | 60 | 60 | 1.7 | 60 | 60 | 60 | 1.4 | 60 | 60 | 60 | 1.4 | 9.3 | 12.2 | 25.7
COURC | COURC380 | 380 | 4.3476 | 50.4946 | 58.6 | 133.1 | 300 | 300 | 81.6 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 101.9 | 300 | 300 | 300 | 58.6 | 116.5 | 280.5 | 300
COUVI | COUVI 70 | 70 | 4.4991 | 50.0663 | 1.4 | 17.6 | 34.5 | 49.3 | 0.4 | 0.9 | 4.8 | 31.3 | 0.9 | 9.6 | 22.7 | 50 | 0.5 | 0.7 | 0.9 | 1.8 | 0.4 | 0.9 | 4.8 | 31.3
CQUIN | CQUIN 36 | 36 | 4.3822 | 50.8504 | 3.6 | 12.3 | 14.5 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 3.6 | 11.8 | 13.6 | 18.3
CQUIN | CQUIN150 | 150 | 4.3822 | 50.8504 | 7.2 | 12.3 | 14.5 | 20.4 | 31.8 | 175 | 175 | 175 | 72.9 | 175 | 175 | 175 | 44.2 | 150.7 | 175 | 175 | 7.2 | 11.8 | 13.6 | 18.3
CROIX | CROIX150 | 150 | 5.2541 | 50.5746 | 3.5 | 36 | 51.8 | 101.6 | 3.3 | 15 | 62.6 | 175 | 5.7 | 175 | 175 | 175 | 3.7 | 8 | 18.6 | 147.8 | 3.3 | 15 | 39.9 | 55.7
DAMPR | DAMPR150 | 150 | 4.4132 | 50.4124 | 10.5 | 29.6 | 39.7 | 63.3 | 14.2 | 74.1 | 153.3 | 175 | 25.5 | 118.4 | 175 | 175 | 35.8 | 89.4 | 166.2 | 175 | 10.5 | 25.1 | 34.1 | 54.4
DEUXA | DEUXA 70 | 70 | 3.853 | 50.7268 | 4.1 | 9.6 | 11.5 | 19.3 | 2 | 3.3 | 50 | 50 | 5.6 | 50 | 50 | 50 | 1.9 | 50 | 50 | 50 | 2 | 3.3 | 11.5 | 13.5
DHANI | DHANI 36 | 36 | 4.3985 | 50.8286 | 4.3 | 20 | 20 | 20 | 8.9 | 20 | 20 | 20 | 12.4 | 20 | 20 | 20 | 16.1 | 20 | 20 | 20 | 4 | 20 | 20 | 20
DHANI | DHANI150 | 150 | 4.3985 | 50.8286 | 11.5 | 86.2 | 140 | 175 | 8.9 | 35.3 | 81.9 | 175 | 12.4 | 33.9 | 63 | 115 | 16.1 | 63.3 | 111.7 | 175 | 6 | 19.5 | 23.5 | 38.6
DIEST | DIEST150 | 150 | 5.0465 | 50.9927 | 3.7 | 6.5 | 9.5 | 30.5 | 47.6 | 175 | 175 | 175 | 149.6 | 175 | 175 | 175 | 72.1 | 175 | 175 | 175 | 3.5 | 6.1 | 8.1 | 15.9
DILSE | DILSE380 | 380 | 5.6831 | 51.0397 | 109.2 | 300 | 300 | 300 | 190.9 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 262.2 | 300 | 300 | 300 | 109.2 | 300 | 300 | 300
DOEL | DOEL 150 | 150 | 4.2559 | 51.3223 | 83.4 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 80.6 | 175 | 175 | 175
DOEL | DOEL 380 | 380 | 4.2559 | 51.3223 | 85.1 | 300 | 300 | 300 | 280.6 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 82.3 | 285.1 | 300 | 300
DORIN | DORIN 70 | 70 | 4.9805 | 50.3061 | 3.9 | 24.9 | 48.4 | 50 | 0.3 | 0.4 | 0.5 | 0.6 | 0.5 | 1.2 | 1.6 | 2.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.3 | 0.4 | 0.5 | 0.6
DROGE | DROGE 36 | 36 | 4.2995 | 50.8035 | 3.8 | 15.9 | 18.9 | 25 | 8.4 | 16.6 | 18.3 | 21.7 | 13.8 | 27.5 | 36.4 | 55.8 | 10.3 | 23.5 | 28.4 | 39.2 | 3.7 | 14.5 | 17.3 | 21.7
DROGE | DROGE150 | 150 | 4.2995 | 50.8035 | 11.4 | 59.8 | 119.6 | 175 | 8.9 | 36.5 | 175 | 175 | 51.1 | 107.7 | 171.5 | 175 | 16.1 | 107.1 | 175 | 175 | 6 | 19.5 | 23.4 | 38.5
DRONG | DRONG 36 | 36 | 3.595 | 51.0401 | 0.5 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0.5 | 20 | 20 | 20
DUINB | DUINB 36 | 36 | 3.2601 | 51.3398 | 9.2 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 5 | 20 | 20 | 20
EEKLN | EEKLN 36 | 36 | 3.5376 | 51.2066 | 12.6 | 60 | 60 | 60 | 6.3 | 41.3 | 60 | 60 | 59.2 | 60 | 60 | 60 | 10.3 | 60 | 60 | 60 | 4.2 | 13.6 | 17.8 | 41.4
EEKLN | EEKLN150 | 150 | 3.5376 | 51.2066 | 21 | 175 | 175 | 175 | 8.2 | 139.3 | 175 | 175 | 60.4 | 175 | 175 | 175 | 22.3 | 175 | 175 | 175 | 7.3 | 56.3 | 167.1 | 175
EEKLO | EEKLO 36 | 36 | 3.5731 | 51.1745 | 1.6 | 50 | 59.9 | 60 | 0.6 | 41.3 | 55.5 | 60 | 1 | 43.5 | 56.2 | 60 | 20 | 60 | 60 | 60 | 0.6 | 9.2 | 12.1 | 27.4
EHEIN | EHEIN 70 | 70 | 5.3908 | 50.573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EISDI | EISDI 70 | 70 | 5.7118 | 51.0062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EKERE | EKERE150 | 150 | 4.4227 | 51.2888 | 4.3 | 5.4 | 6 | 6.8 | 5.9 | 12.8 | 24.7 | 61.6 | 7.6 | 14.1 | 17.3 | 28.5 | 6.9 | 26.7 | 43 | 137.3 | 4.3 | 5.2 | 5.7 | 6.5
ENGIS | ENGIS 70 | 70 | 5.3739 | 50.5666 | 1.5 | 3.2 | 8.8 | 38.3 | 1.7 | 31.4 | 46.4 | 50 | 2.8 | 50 | 50 | 50 | 2.3 | 50 | 50 | 50 | 1.5 | 2.3 | 3.4 | 19.2
ERTVE | ERTVE 36 | 36 | 3.7568 | 51.1771 | 7.6 | 20 | 20 | 20 | 0.7 | 20 | 20 | 20 | 1.2 | 20 | 20 | 20 | 1 | 20 | 20 | 20 | 0.7 | 9.2 | 12.1 | 20
ESNEU | ESNEU 70 | 70 | 5.5996 | 50.5286 | 0.7 | 1.2 | 2.3 | 18.3 | 0.7 | 6.8 | 13 | 50 | 1.2 | 50 | 50 | 50 | 1 | 37.3 | 50 | 50 | 0.7 | 1.2 | 1.9 | 13.3
ESPIN | ESPIN 36 | 36 | 4.3824 | 50.7579 | 2.8 | 20 | 20 | 20 | 4.8 | 16.9 | 20 | 20 | 10.2 | 20 | 20 | 20 | 5.3 | 11.8 | 20 | 20 | 2.7 | 16.9 | 20 | 20
ESSEG | ESSEG 36 | 36 | 4.3365 | 50.881 | 0.8 | 12.3 | 14.7 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0.8 | 11.8 | 13.6 | 18.4
ESSNE | ESSNE 70 | 70 | 4.125 | 50.8939 | 1.8 | 11.6 | 22.1 | 39.6 | 1.4 | 26.8 | 36.7 | 50 | 14 | 50 | 50 | 50 | 7.4 | 34.1 | 50 | 50 | 1.4 | 2 | 2.2 | 2.6
EUPEN | EUPEN 70 | 70 | 6.0217 | 50.6311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
FAYSV | FAYSV 70 | 70 | 5.1596 | 49.8636 | 0.4 | 1.2 | 6.6 | 20.9 | 0.4 | 0.6 | 0.8 | 3.6 | 0.5 | 1 | 1.3 | 1.9 | 0.5 | 0.8 | 1 | 1.8 | 0.4 | 0.6 | 0.8 | 3.6
FLEIN | FLEIN220 | 220 | 5.4619 | 50.5901 | 12.6 | 31.8 | 48.3 | 120.3 | 9.2 | 21.1 | 41.8 | 175 | 16.2 | 175 | 175 | 175 | 22.9 | 175 | 175 | 175 | 9.2 | 21.1 | 27.4 | 38.7
FLORA | FLORA 36 | 36 | 3.7493 | 51.0211 | 2.3 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 2 | 4.4 | 8.3 | 16
FLORE | FLORE 70 | 70 | 5.0809 | 50.3862 | 1.4 | 2.5 | 6.4 | 42.3 | 0.7 | 5.4 | 21.4 | 49.7 | 1.2 | 19.9 | 50 | 50 | 0.8 | 1.5 | 3.1 | 14.5 | 0.7 | 2.1 | 3.5 | 18.2
FOOZ | FOOZ 70 | 70 | 5.436 | 50.6854 | 1.6 | 3.5 | 9.7 | 39.2 | 1.8 | 30 | 44.2 | 50 | 2.9 | 50 | 50 | 50 | 2.5 | 41.5 | 50 | 50 | 1.1 | 3.2 | 9.4 | 28.1
FORES | FORES150 | 150 | 4.3268 | 50.8076 | 7.8 | 87.3 | 140.2 | 175 | 8.9 | 35.2 | 81.8 | 175 | 12.4 | 33.9 | 62.8 | 114.7 | 16.1 | 63.7 | 112.7 | 175 | 5.2 | 34.4 | 81.8 | 175
GASTH | GASTH 70 | 70 | 4.6745 | 50.8843 | 1.5 | 9.3 | 13 | 18.5 | 22.5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 39 | 50 | 50 | 50 | 1.5 | 8.3 | 11.3 | 16
GEMBL | GEMBL 70 | 70 | 4.6636 | 50.5506 | 0.4 | 0.8 | 3 | 17.8 | 0.4 | 0.6 | 0.7 | 1.3 | 0.6 | 1.4 | 2.6 | 25.1 | 0.5 | 0.7 | 0.9 | 1.3 | 0.4 | 0.6 | 0.7 | 1.3
GERDI | GERDI 70 | 70 | 5.5813 | 51.1391 | 2.8 | 24.9 | 35.1 | 50 | 9.2 | 26.8 | 50 | 50 | 50 | 50 | 50 | 50 | 13.8 | 50 | 50 | 50 | 2.5 | 17.8 | 26.1 | 39.2
GEZEL | GEZEL380 | 380 | 3.2012 | 51.2639 | 107.4 | 300 | 300 | 300 | 142.6 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 163.2 | 300 | 300 | 300 | 107.4 | 300 | 300 | 300
GISTE | GISTE 36 | 36 | 2.9545 | 51.1509 | 7.5 | 20 | 20 | 20 | 7.2 | 20 | 20 | 20 | 11.6 | 20 | 20 | 20 | 17.9 | 20 | 20 | 20 | 1.1 | 1.4 | 1.6 | 2
GODSH | GODSH 70 | 70 | 5.3746 | 50.9257 | 3.2 | 18.9 | 25.1 | 39.2 | 7.7 | 22 | 50 | 50 | 50 | 50 | 50 | 50 | 11.7 | 50 | 50 | 50 | 1.6 | 22 | 33.7 | 50
GODSH | GODSH150 | 150 | 5.3746 | 50.9257 | 12.6 | 22.6 | 26 | 35.4 | 36.8 | 175 | 175 | 175 | 51.9 | 175 | 175 | 175 | 146.7 | 175 | 175 | 175 | 11.8 | 21.6 | 24 | 29.7
GOUY | GOUY 150 | 150 | 4.3322 | 50.4826 | 15.9 | 32.3 | 81.5 | 215.7 | 33 | 86.9 | 117.1 | 173.8 | 94.9 | 300 | 300 | 300 | 35.9 | 80.4 | 167.1 | 300 | 15.9 | 29 | 49.4 | 139.9
GOUY | GOUY 70 | 70 | 4.3322 | 50.4826 | 1.5 | 33.5 | 51 | 60 | 11.4 | 28.9 | 53.9 | 60 | 60 | 60 | 60 | 60 | 16.7 | 36.4 | 60 | 60 | 1.5 | 22.1 | 35.2 | 60
GRAMM | GRAMM150 | 150 | 5.2865 | 50.5123 | 7.8 | 19.6 | 41.1 | 112.7 | 7.3 | 11.8 | 19.2 | 50.1 | 9.5 | 37.2 | 60.5 | 155.6 | 8.7 | 19 | 36.2 | 94.9 | 7.3 | 11.8 | 19.2 | 50.1
GRAMM | GRAMM380 | 380 | 5.2865 | 50.5123 | 67 | 300 | 300 | 300 | 42.5 | 253.5 | 300 | 300 | 255.7 | 300 | 300 | 300 | 54.9 | 300 | 300 | 300 | 42.5 | 253.5 | 300 | 300
HAM | HAM 36 | 36 | 3.7351 | 51.0605 | 7.6 | 60 | 60 | 60 | 2.6 | 60 | 60 | 60 | 57.9 | 60 | 60 | 60 | 4.2 | 60 | 60 | 60 | 2.6 | 9.4 | 12.7 | 29.7
HANNU | HANNU150 | 150 | 5.0921 | 50.6742 | 3.5 | 39.2 | 54.8 | 114.3 | 3.3 | 14.1 | 56.4 | 145.1 | 5.7 | 175 | 175 | 175 | 3.7 | 8 | 18.3 | 150.4 | 3.3 | 14.1 | 38.5 | 55.6
HANZI | HANZI 70 | 70 | 4.5584 | 50.2867 | 1.9 | 8.9 | 28 | 46.5 | 1.1 | 42 | 50 | 50 | 1.8 | 31.9 | 50 | 50 | 1.2 | 6.6 | 38 | 50 | 1.1 | 7.7 | 22.1 | 38.9
HAREL | HAREL 36 | 36 | 3.3123 | 50.8665 | 1.2 | 30 | 60 | 60 | 6.4 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 34.2 | 60 | 60 | 60 | 1.2 | 28.9 | 55.3 | 60
HARMI | HARMI 70 | 70 | 4.0193 | 50.415 | 5.1 | 33.4 | 42.5 | 50 | 1.6 | 2.8 | 5.3 | 33.2 | 3.1 | 50 | 50 | 50 | 1.9 | 2.8 | 3.4 | 5.2 | 1.6 | 2.8 | 5.3 | 33.2
HARMI | HARMI150 | 150 | 4.0193 | 50.415 | 5.1 | 33.4 | 42.5 | 75.6 | 1.6 | 2.8 | 5.3 | 33.2 | 3.1 | 72.7 | 107.9 | 161.5 | 1.9 | 2.8 | 3.4 | 5.2 | 1.6 | 2.8 | 5.3 | 33.2
HARYD | HARYD 36 | 36 | 4.4245 | 50.8891 | 4.7 | 10.7 | 13.9 | 19.9 | 1.5 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 11.3 | 20 | 20 | 20 | 1.5 | 6.4 | 8.5 | 17.2
HASTI | HASTI 70 | 70 | 4.8201 | 50.2118 | 0.4 | 2.1 | 8.7 | 29.7 | 0.4 | 4.1 | 8.8 | 30.8 | 0.7 | 6.7 | 17.1 | 30.6 | 0.5 | 0.9 | 1.8 | 25.4 | 0.4 | 1.2 | 7.3 | 26.8
HAVE7 | HAVE7150 | 150 | 4.3865 | 51.2879 | 4.2 | 4.9 | 5.2 | 6 | 12.8 | 17.4 | 23.2 | 57.7 | 16.2 | 33.1 | 44.3 | 68.7 | 14.1 | 25 | 40.3 | 128.7 | 4.2 | 4.9 | 5.2 | 5.9
HECHT | HECHT 70 | 70 | 5.3931 | 51.1303 | 4.6 | 20 | 28.2 | 39.5 | 6.5 | 15.2 | 50 | 50 | 50 | 50 | 50 | 50 | 9.8 | 50 | 50 | 50 | 3.7 | 11.9 | 21.4 | 30.5
HEIMO | HEIMO150 | 150 | 4.136 | 51.1414 | 3.6 | 13.8 | 19.5 | 52 | 11.1 | 13.3 | 14.5 | 17.8 | 19.6 | 61.6 | 80.2 | 126.3 | 12.7 | 19.2 | 23.5 | 32.8 | 3.2 | 12.3 | 14.5 | 17.8
HEINS | HEINS 70 | 70 | 5.7552 | 49.6935 | 1.2 | 4.3 | 14.3 | 50 | 1.7 | 3.9 | 6.5 | 20.6 | 2.2 | 5.2 | 7.8 | 14 | 2.9 | 18.9 | 37.4 | 50 | 1.2 | 2.4 | 3.1 | 5.9
HEINS | HEINS220 | 220 | 5.7552 | 49.6935 | 4.4 | 6.3 | 9.6 | 55.7 | 4.4 | 7.4 | 16.3 | 175 | 14.4 | 175 | 175 | 175 | 6.6 | 131.2 | 175 | 175 | 4.4 | 6.3 | 9.6 | 50.9
HELIA | HELIA 36 | 36 | 4.3517 | 50.8586 | 12.9 | 20 | 20 | 20 | 13.6 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 3.3 | 20 | 20 | 20
HELIB | HELIB 36 | 36 | 4.3517 | 50.8586 | 3.9 | 12.3 | 14.7 | 20 | 3.4 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 4.9 | 20 | 20 | 20 | 2.1 | 11.8 | 13.6 | 18.4
HELIP | HELIP150 | 150 | 4.3517 | 50.8586 | 12.9 | 25.1 | 38.3 | 122 | 31.8 | 117 | 175 | 175 | 100.2 | 175 | 175 | 175 | 50.2 | 175 | 175 | 175 | 3.3 | 23.2 | 35.3 | 120.5
HEOUT | HEOUT 70 | 70 | 4.7986 | 51.1563 | 0.6 | 3.9 | 11.2 | 30 | 10.7 | 27.2 | 33.3 | 50 | 44.2 | 50 | 50 | 50 | 17.3 | 50 | 50 | 50 | 0.6 | 3.7 | 11.2 | 34
HERBA | HERBA 70 | 70 | 5.5503 | 50.0494 | 0.3 | 4 | 7.9 | 20.8 | 0.3 | 1.5 | 5.3 | 18.9 | 2.6 | 39.3 | 50 | 50 | 0.5 | 4.1 | 10 | 24.2 | 0.3 | 1.5 | 5.3 | 18.9
HERDE | HERDE150 | 150 | 5.5616 | 50.802 | 6 | 33.2 | 43.7 | 74.1 | 16.2 | 43.3 | 65.7 | 175 | 31.9 | 73.3 | 120.3 | 175 | 29.5 | 150.9 | 175 | 175 | 6 | 26.6 | 33.6 | 46.2
HEREN | HEREN 70 | 70 | 4.8683 | 51.1796 | 5.2 | 7.3 | 10.1 | 32.7 | 2.6 | 26.9 | 32.9 | 50 | 35.8 | 50 | 50 | 50 | 2.8 | 46.8 | 50 | 50 | 2.6 | 7.3 | 10.1 | 30.3
HEREN | HEREN150 | 150 | 4.8683 | 51.1796 | 2.3 | 3.3 | 4.8 | 19.2 | 6.9 | 26.8 | 33.1 | 53 | 36.4 | 175 | 175 | 175 | 16.3 | 47.5 | 63.4 | 102.9 | 2.3 | 3.3 | 4.8 | 18.3
HERST | HERST 70 | 70 | 5.6286 | 50.6779 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HEULE | HEULE 70 | 70 | 3.2489 | 50.8335 | 2.5 | 4.1 | 6.6 | 36.9 | 2.5 | 50 | 50 | 50 | 3.3 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1.3 | 5.5 | 14.5 | 32.8
HEVRL | HEVRL 70 | 70 | 4.7184 | 50.8548 | 1.5 | 9 | 12 | 18 | 34.6 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1.5 | 8 | 10.8 | 15.7
HEZE | HEZE 150 | 150 | 4.9446 | 51.1369 | 4.9 | 7.4 | 9.7 | 23 | 11.2 | 24.2 | 29.9 | 43.2 | 28.4 | 119.3 | 175 | 175 | 12.1 | 41.3 | 54.6 | 90 | 4.9 | 7.5 | 10.1 | 24
HOOGS | HOOGS 36 | 36 | 4.7503 | 51.3902 | 4.5 | 20 | 20 | 20 | 4.1 | 8.7 | 14.3 | 20 | 8.2 | 15.5 | 20 | 20 | 5.6 | 16.8 | 20 | 20 | 4.1 | 8.7 | 14.3 | 20
HORTA | HORTA380 | 380 | 3.6037 | 51.1146 | 109.4 | 300 | 300 | 300 | 146.4 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 167.6 | 300 | 300 | 300 | 109.4 | 300 | 300 | 300
HOUFF | HOUFF 70 | 70 | 5.7951 | 50.1501 | 6.1 | 11 | 14.7 | 38.3 | 0.5 | 0.7 | 0.8 | 1.3 | 0.7 | 1.8 | 2.4 | 4.1 | 0.6 | 0.9 | 1.1 | 1.5 | 0.5 | 0.7 | 0.8 | 1.3
HOUTH | HOUTH 70 | 70 | 5.3713 | 51.0295 | 3.5 | 16 | 23.4 | 34.9 | 5.4 | 12.6 | 50 | 50 | 24.9 | 50 | 50 | 50 | 8.1 | 50 | 50 | 50 | 2.9 | 9.2 | 18.4 | 25.8
HOUTW | HOUTW 36 | 36 | 4.4157 | 50.882 | 4.7 | 10.7 | 13.8 | 19.7 | 18.6 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0.3 | 6.4 | 8.5 | 17.1
HOVES | HOVES 70 | 70 | 4.0316 | 50.6795 | 1.2 | 3.3 | 5.4 | 11.7 | 1.2 | 3.3 | 4.6 | 6.2 | 4.3 | 16.5 | 21.2 | 31.8 | 1.5 | 2.8 | 4.3 | 7 | 0.9 | 2.2 | 3.4 | 6.2
HULDN | HULDN 36 | 36 | 4.5999 | 50.7815 | 0.5 | 20 | 20 | 20 | 4.4 | 16.2 | 20 | 20 | 7.5 | 20 | 20 | 20 | 5.6 | 13.6 | 20 | 20 | 0.5 | 11.2 | 20 | 20
IEPER | IEPER150 | 150 | 2.8594 | 50.8477 | 3.2 | 34.9 | 66.6 | 101.2 | 24.9 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 34.3 | 175 | 175 | 175 | 3 | 27.1 | 53.4 | 92.4
IL1BL | IL1BL220 | 220 | 2.49 | 51.53 | 105.5 | 175 | 175 | 175 | 0 | 0 | 0 | 175 | 0 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 0 | 0 | 0 | 175
IL1RD | IL1RD220 | 220 | 2.49 | 51.53 | 105.5 | 175 | 175 | 175 | 0 | 0 | 0 | 175 | 0 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 0 | 0 | 0 | 175
IXELL | IXELL 36 | 36 | 4.3949 | 50.8141 | 4.2 | 60 | 60 | 60 | 8.9 | 35.3 | 60 | 60 | 12.4 | 33.9 | 60 | 60 | 16.1 | 60 | 60 | 60 | 4 | 34.4 | 60 | 60
IXELL | IXELL150 | 150 | 4.3949 | 50.8141 | 11.5 | 86.6 | 140.4 | 175 | 8.9 | 35.2 | 81.8 | 175 | 12.4 | 33.9 | 62.9 | 114.8 | 16.1 | 63.2 | 111.6 | 175 | 6 | 19.5 | 23.5 | 38.7
IZGEM | IZGEM150 | 150 | 3.2264 | 50.8972 | 20.7 | 36.6 | 122 | 300 | 25.3 | 49 | 68.3 | 169 | 133.1 | 300 | 300 | 300 | 27.4 | 60.3 | 76.8 | 121.2 | 15.9 | 34.1 | 68.3 | 169
IZGEM | IZGEM380 | 380 | 3.2264 | 50.8972 | 103.5 | 300 | 300 | 300 | 135.1 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 154.7 | 300 | 300 | 300 | 103.5 | 300 | 300 | 300
JEMAP | JEMAP 70 | 70 | 3.8717 | 50.4545 | 1.4 | 2.4 | 3 | 3.9 | 1.3 | 6.2 | 7.7 | 9.8 | 2.3 | 21.6 | 28.1 | 40.2 | 1.4 | 5.9 | 7.8 | 14.4 | 1.3 | 2.2 | 2.7 | 3.6
JOSAP | JOSAP 36 | 36 | 4.3931 | 50.8612 | 0.3 | 11.9 | 13.8 | 17.1 | 2.3 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0.3 | 11.5 | 13.1 | 16.5
JUPIL | JUPIL220 | 220 | 5.6196 | 50.6445 | 12.9 | 21.1 | 32 | 67.6 | 14 | 28.5 | 56.9 | 175 | 34.8 | 175 | 175 | 175 | 21.2 | 175 | 175 | 175 | 12.9 | 18.7 | 22.1 | 32.3
KALLO | KALLO 36 | 36 | 4.2888 | 51.2533 | 3.1 | 9.8 | 10.6 | 12.7 | 7.7 | 13.5 | 14.9 | 18.7 | 13.9 | 25.1 | 30 | 40.4 | 8.3 | 18.9 | 23.2 | 36.7 | 3.1 | 3.8 | 4.6 | 7.8
KALLO | KALLO150 | 150 | 4.2888 | 51.2533 | 4.2 | 9.8 | 10.6 | 12.7 | 7.7 | 13.5 | 14.9 | 18.7 | 13.9 | 25.1 | 30 | 40.4 | 8.3 | 18.9 | 23.2 | 36.8 | 4.2 | 6.8 | 7.4 | 9
KENNE | KENNE 36 | 36 | 3.7821 | 51.1285 | 7.6 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 2.3 | 9.4 | 12.5 | 20
KERSB | KERSB150 | 150 | 4.993 | 50.8921 | 4.9 | 14.1 | 42.6 | 79.3 | 52.8 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 110.9 | 175 | 175 | 175 | 4.8 | 10 | 19 | 38.2
KETEN | KETEN 36 | 36 | 4.2789 | 51.2694 | 3.1 | 9.8 | 10.6 | 12.7 | 7.7 | 13.5 | 14.9 | 18.7 | 13.9 | 25.1 | 30 | 40.4 | 8.3 | 18.9 | 23.2 | 36.7 | 3.1 | 3.8 | 4.6 | 7.8
KETEN | KETEN150 | 150 | 4.2789 | 51.2694 | 3.1 | 9.8 | 10.6 | 12.7 | 7.7 | 13.5 | 14.9 | 18.7 | 13.9 | 25.1 | 30 | 40.4 | 8.3 | 18.9 | 23.2 | 36.8 | 3.1 | 3.8 | 4.6 | 7.8
KLUDO | KLUDO 36 | 36 | 3.7671 | 51.149 | 7.6 | 60 | 60 | 60 | 6.7 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 11.1 | 60 | 60 | 60 | 6.5 | 9.2 | 12 | 27.4
KLUDO | KLUDO150 | 150 | 3.7671 | 51.149 | 7.6 | 175 | 175 | 175 | 6.7 | 175 | 175 | 175 | 64.2 | 175 | 175 | 175 | 11.1 | 175 | 175 | 175 | 6.5 | 9.2 | 12 | 27.4
KOKSI | KOKSI150 | 150 | 2.6751 | 51.1105 | 10.8 | 53.2 | 128.5 | 175 | 8.1 | 175 | 175 | 175 | 20.3 | 175 | 175 | 175 | 40.9 | 175 | 175 | 175 | 7.5 | 22 | 77.8 | 128.7
KOOST | KOOST 70 | 70 | 3.2942 | 50.8258 | 2.7 | 21.7 | 29.3 | 37.3 | 2.5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1.2 | 5.8 | 15 | 29.9
KUURN | KUURN 70 | 70 | 3.264 | 50.8593 | 2.4 | 3.8 | 6.1 | 37.3 | 2.5 | 50 | 50 | 50 | 3.1 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1.4 | 5.1 | 13.8 | 29.2
KWATW | KWATW 36 | 36 | 3.8285 | 50.9929 | 2.3 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0.7 | 4.4 | 14.6 | 20
LACRO | LACRO150 | 150 | 4.1917 | 50.4941 | 6.1 | 22.8 | 31.6 | 54.2 | 24.5 | 54 | 74.1 | 115.4 | 63.5 | 175 | 175 | 175 | 35.1 | 72.9 | 149.1 | 175 | 5.2 | 19.5 | 26.4 | 46.3
LANAI | LANAI 70 | 70 | 5.6607 | 50.8873 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LANAK | LANAK150 | 150 | 5.6435 | 50.8834 | 9.1 | 52.1 | 144.9 | 175 | 53.1 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 86.1 | 175 | 175 | 175 | 9.1 | 25.5 | 31.5 | 40.7
LANGE | LANGE150 | 150 | 3.7412 | 51.1162 | 7.6 | 175 | 175 | 175 | 100.8 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 119.7 | 175 | 175 | 175 | 5.9 | 9.3 | 12.2 | 26.2
LANLO | LANLO 70 | 70 | 5.512 | 50.9384 | 10 | 43.1 | 60 | 60 | 9.4 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 10.1 | 60 | 60 | 60 | 8.7 | 51.8 | 60 | 60
LANLO | LANLO150 | 150 | 5.512 | 50.9384 | 9.1 | 45.7 | 145.3 | 175 | 120 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 9.1 | 45.2 | 127.5 | 175
LENS | LENS 70 | 70 | 3.9031 | 50.5651 | 1.1 | 3.9 | 4.9 | 6.5 | 1.1 | 5 | 7.4 | 11.9 | 1.9 | 9.5 | 13.3 | 24.2 | 1.6 | 5.1 | 7 | 11.4 | 1 | 2.3 | 2.9 | 3.9
LEUZE | LEUZE 70 | 70 | 4.9119 | 50.5518 | 1.1 | 5.8 | 17.4 | 50 | 0.7 | 1.5 | 4.3 | 21.9 | 1.4 | 7.3 | 24.5 | 50 | 0.8 | 1.2 | 1.6 | 3.5 | 0.7 | 1.5 | 4.3 | 21.9
LEVAL | LEVAL220 | 220 | 5.4927 | 50.6042 | 12.8 | 31.4 | 47.8 | 119.8 | 7.3 | 18 | 38.1 | 175 | 12.8 | 175 | 175 | 175 | 18.1 | 175 | 175 | 175 | 7.3 | 18 | 27.3 | 38.5
LIBER | LIBER 70 | 70 | 4.4296 | 50.5151 | 4.5 | 18.5 | 25.9 | 43.8 | 0.3 | 0.4 | 0.5 | 0.7 | 0.5 | 1.1 | 1.4 | 2 | 0.4 | 0.6 | 0.7 | 0.9 | 0.3 | 0.4 | 0.5 | 0.7
LICHT | LICHT 36 | 36 | 3.1223 | 51.0248 | 0.2 | 1.8 | 2.6 | 3.5 | 0 | 20 | 20 | 20 | 0 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0 | 1.8 | 2.5 | 3.5
LIGNE | LIGNE 70 | 70 | 3.7014 | 50.6274 | 1.5 | 4.3 | 6.6 | 11.4 | 1.8 | 3 | 3.7 | 5.6 | 6.6 | 19.7 | 22.6 | 29.4 | 2 | 4.1 | 5.6 | 9.1 | 1.5 | 3 | 3.7 | 5.6
LILLO | LILLO 36 | 36 | 4.307 | 51.3013 | 8.5 | 9.8 | 10.6 | 12.7 | 7.7 | 13.5 | 14.9 | 18.7 | 13.9 | 25.1 | 30 | 40.4 | 8.3 | 18.9 | 23.2 | 36.8 | 7.7 | 9.8 | 10.6 | 12.5
LILLO | LILLO150 | 150 | 4.307 | 51.3013 | 8.5 | 102.3 | 137.2 | 216.2 | 7.7 | 110.7 | 137.4 | 181.9 | 53 | 294.5 | 300 | 300 | 8.3 | 173.7 | 254.7 | 300 | 7.7 | 100 | 126.4 | 181.9
LILLO | LILLO380 | 380 | 4.307 | 51.3013 | 83.3 | 300 | 300 | 300 | 177.1 | 300 | 300 | 300 | 281.3 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 80.5 | 272.8 | 300 | 300
LINT | LINT 150 | 150 | 4.5087 | 51.1176 | 13.2 | 43.2 | 90.1 | 182.5 | 9.7 | 26.2 | 50.3 | 153.4 | 17 | 46 | 58.3 | 105.8 | 11.2 | 34.8 | 95.5 | 249.4 | 9.7 | 15.6 | 50.3 | 153.4
LIXHE | LIXHE150 | 150 | 5.6692 | 50.754 | 7.5 | 33.3 | 45.7 | 76.8 | 8.6 | 46 | 69.4 | 209.2 | 26.4 | 60.7 | 101.1 | 300 | 27.4 | 182.3 | 276.2 | 300 | 7.5 | 27 | 34.8 | 49.5
LIXHE | LIXHE220 | 220 | 5.6692 | 50.754 | 9.2 | 15.8 | 25.9 | 61.3 | 9.2 | 18.3 | 33.7 | 163.5 | 17.8 | 175 | 175 | 175 | 13.8 | 114.6 | 175 | 175 | 9.2 | 14.2 | 18.1 | 30.8
LIXHE | LIXHE380 | 380 | 5.6692 | 50.754 | 37.9 | 76.5 | 146.2 | 300 | 24.9 | 242.5 | 300 | 300 | 193.6 | 300 | 300 | 300 | 36 | 284.1 | 300 | 300 | 24.9 | 57.5 | 91.9 | 300
LOBBE | LOBBE 70 | 70 | 4.2607 | 50.3582 | 1.5 | 17.1 | 42.4 | 50 | 11 | 30.6 | 50 | 50 | 50 | 50 | 50 | 50 | 16.7 | 36.4 | 50 | 50 | 1.5 | 11.2 | 34.5 | 50
LOEWP | LOEWP 36 | 36 | 4.7162 | 51.445 | 4.3 | 20 | 20 | 20 | 4.1 | 8.8 | 13.3 | 20 | 7.9 | 15.4 | 19.7 | 20 | 5.6 | 15.1 | 20 | 20 | 4.1 | 8.8 | 13.3 | 20
LOKER | LOKER 36 | 36 | 3.9799 | 51.1062 | 8 | 13.8 | 20 | 20 | 11.1 | 13.3 | 14.6 | 18 | 20 | 20 | 20 | 20 | 12.7 | 19.2 | 20 | 20 | 3.2 | 12 | 14.6 | 18
LOUVA | LOUVA 36 | 36 | 4.6186 | 50.6708 | 1.2 | 20 | 20 | 20 | 1.9 | 16.6 | 20 | 20 | 7.5 | 20 | 20 | 20 | 2.7 | 20 | 20 | 20 | 1.1 | 10.4 | 19.3 | 20
MAASE | MAASE 70 | 70 | 5.7844 | 51.0922 | 1.5 | 33.1 | 46.6 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1.3 | 21.5 | 31 | 45.9
MAASM | MAASM 70 | 70 | 5.6954 | 50.9476 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
MACHE | MACHE 36 | 36 | 4.4275 | 50.9172 | 4.7 | 10.7 | 13.8 | 18.5 | 25.4 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 35.3 | 60 | 60 | 60 | 4.7 | 6.4 | 8.5 | 15.7
MACHE | MACHE150 | 150 | 4.4275 | 50.9172 | 4.7 | 10.7 | 13.8 | 18.5 | 25.4 | 175 | 175 | 175 | 72.9 | 175 | 175 | 175 | 35.3 | 175 | 175 | 175 | 4.7 | 6.4 | 8.5 | 15.7
MAERL | MAERL380 | 380 | 3.3158 | 51.227 | 107.7 | 300 | 300 | 300 | 143 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 163.7 | 300 | 300 | 300 | 107.6 | 300 | 300 | 300
MALDR | MALDR 70 | 70 | 4.2649 | 51.022 | 3.3 | 20.8 | 29.4 | 58.7 | 18.6 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 31 | 60 | 60 | 60 | 1.6 | 2 | 2.6 | 8.6
MALEC | MALEC150 | 150 | 4.2218 | 50.556 | 5.3 | 26.7 | 34.3 | 58.8 | 30.5 | 70.2 | 92.4 | 130.5 | 85.3 | 175 | 175 | 175 | 33.9 | 75.3 | 156.8 | 175 | 5 | 24.8 | 31.7 | 49.6
MARCO | MARCO 70 | 70 | 5.5502 | 50.21 | 0.7 | 3.7 | 13.4 | 35 | 1 | 10.6 | 19.8 | 50 | 4.8 | 50 | 50 | 50 | 1.1 | 39.9 | 50 | 50 | 0.7 | 3.7 | 12.7 | 29.9
MARFA | MARFA 70 | 70 | 5.3454 | 50.2369 | 3.8 | 8 | 25 | 50 | 2 | 9.2 | 45.7 | 50 | 4.7 | 50 | 50 | 50 | 3.9 | 14.6 | 25 | 50 | 2 | 8 | 25 | 50
MARLD | MARLD 70 | 70 | 4.9744 | 50.4795 | 1.1 | 2.7 | 4.2 | 24.8 | 0.6 | 4 | 24.2 | 45.7 | 1 | 8.1 | 35.2 | 50 | 0.7 | 2.5 | 3.9 | 7.6 | 0.6 | 2.3 | 3.2 | 6.6
MASSE | MASSE150 | 150 | 4.6292 | 51.1958 | 7.5 | 49.8 | 136.8 | 175 | 6.8 | 14.3 | 22.4 | 118.4 | 13.9 | 59.5 | 120 | 175 | 9.5 | 29.6 | 58.3 | 172.8 | 6.8 | 14.3 | 22.4 | 118.4
MASSE | MASSE380 | 380 | 4.6292 | 51.1958 | 71.1 | 136.7 | 300 | 300 | 176.5 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 71.1 | 131.1 | 254.3 | 300
MEERH | MEERH150 | 150 | 5.0632 | 51.1073 | 7.6 | 41.2 | 69.7 | 87.1 | 11.9 | 46.6 | 217.5 | 300 | 48.6 | 300 | 300 | 300 | 19 | 73.2 | 130.2 | 300 | 7.6 | 41.2 | 69.7 | 87.1
MEERH | MEERH380 | 380 | 5.0632 | 51.1073 | 45.6 | 185.2 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 45.6 | 155.9 | 300 | 300
MERCA | MERCA150 | 150 | 4.2468 | 51.1541 | 8.5 | 12.3 | 14.9 | 25.8 | 11.1 | 13.3 | 14.5 | 17.8 | 19.6 | 60.3 | 78.2 | 121.5 | 12.7 | 19.2 | 23.5 | 32.8 | 8 | 11.9 | 13.9 | 17.8
MERCA | MERCA380 | 380 | 4.2468 | 51.1541 | 83.2 | 300 | 300 | 300 | 266.3 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 80.4 | 257.8 | 300 | 300
MERCH | MERCH 70 | 70 | 4.2235 | 50.9653 | 3.3 | 19.8 | 42 | 50 | 1.4 | 12.5 | 28.6 | 50 | 10.9 | 50 | 50 | 50 | 2.3 | 7.8 | 28.3 | 50 | 1.4 | 2 | 2.1 | 2.6
MERKS | MERKS150 | 150 | 4.457 | 51.2398 | 6.5 | 42.8 | 99 | 175 | 7.5 | 23.6 | 46 | 175 | 17.5 | 41.7 | 59.1 | 104.3 | 12 | 37.7 | 82.8 | 175 | 6.1 | 19.4 | 46 | 163.5
MIDI | MIDI 150 | 150 | 4.3241 | 50.8279 | 11.6 | 89.1 | 142.6 | 175 | 8.9 | 35.4 | 82.2 | 175 | 12.4 | 33.9 | 63.2 | 115.4 | 16.1 | 64 | 113.2 | 175 | 6 | 19.5 | 23.5 | 38.8
MIDI | MIDI 36 | 36 | 4.3241 | 50.8279 | 4 | 7.9 | 8.7 | 10.3 | 3.7 | 20 | 20 | 20 | 7.6 | 20 | 20 | 20 | 4 | 20 | 20 | 20 | 3.7 | 8.2 | 9 | 10.7
MIECR | MIECR 70 | 70 | 5.2329 | 50.3698 | 1.3 | 2.5 | 4.6 | 14.9 | 0.2 | 0.3 | 0.4 | 1 | 0.4 | 1.3 | 2.3 | 7.2 | 0.3 | 0.4 | 0.5 | 0.7 | 0.2 | 0.3 | 0.4 | 1
MOARD | MOARD 70 | 70 | 4.9849 | 49.909 | 0.4 | 1.2 | 2.6 | 9.5 | 0.4 | 0.6 | 0.8 | 2.9 | 0.5 | 1 | 1.3 | 1.9 | 0.5 | 0.8 | 1.2 | 2 | 0.4 | 0.6 | 0.8 | 2.9
MOL | MOL 150 | 150 | 5.1081 | 51.2213 | 6.5 | 17.5 | 30.8 | 125.5 | 11.8 | 175 | 175 | 175 | 28.2 | 148.7 | 175 | 175 | 17.2 | 175 | 175 | 175 | 6.5 | 12.5 | 24.7 | 97.7
MOLEN | MOLEN 36 | 36 | 4.3249 | 50.852 | 12.9 | 25.1 | 38.3 | 60 | 13.6 | 60 | 60 | 60 | 43.3 | 60 | 60 | 60 | 24.9 | 60 | 60 | 60 | 3.3 | 23.2 | 35.3 | 60
MOLEN | MOLEN150 | 150 | 4.3249 | 50.852 | 12.9 | 25.1 | 38.3 | 122 | 13.6 | 70.6 | 175 | 175 | 43.3 | 118.3 | 175 | 175 | 24.9 | 175 | 175 | 175 | 3.3 | 23.2 | 35.3 | 120.5
MONCE | MONCE150 | 150 | 4.3739 | 50.396 | 9 | 29.3 | 38.8 | 62.4 | 11.9 | 69.7 | 137.7 | 175 | 21.4 | 85 | 175 | 175 | 25.7 | 89.5 | 159.5 | 175 | 9 | 24.6 | 33.5 | 54.6
MONS | MONS 70 | 70 | 3.9458 | 50.4612 | 1.2 | 2.5 | 3.1 | 4.2 | 1.2 | 9.3 | 11 | 14.4 | 2.1 | 45.1 | 50 | 50 | 1.7 | 12.9 | 15.6 | 23.4 | 1.2 | 2.3 | 2.9 | 4
MONTI | MONTI150 | 150 | 4.4614 | 50.4019 | 4.8 | 17 | 41 | 101.9 | 4.9 | 54.4 | 127.4 | 175 | 8.8 | 25.6 | 62 | 175 | 7.5 | 55.1 | 135.1 | 175 | 4.8 | 11.1 | 25.1 | 78.6
MORTS | MORTS150 | 150 | 4.4698 | 51.176 | 5 | 90.1 | 167.8 | 175 | 9 | 42.2 | 99.5 | 175 | 17.7 | 80.1 | 175 | 175 | 15.3 | 47.3 | 97.8 | 175 | 3.9 | 12.4 | 63.4 | 137.7
MOUSC | MOUSC150 | 150 | 3.2477 | 50.7565 | 15.2 | 26.8 | 95.8 | 175 | 9 | 175 | 175 | 175 | 80.6 | 175 | 175 | 175 | 8.8 | 175 | 175 | 175 | 9 | 25.8 | 50.6 | 128.8
NAMUR | NAMUR 70 | 70 | 4.835 | 50.4617 | 1.1 | 4.9 | 9.2 | 32.3 | 2 | 5.2 | 8.4 | 16.9 | 3.7 | 50 | 50 | 50 | 2.3 | 3.7 | 6.1 | 13.1 | 1.1 | 5.1 | 8.4 | 16.9
NEUFC | NEUFC 70 | 70 | 5.4448 | 49.8578 | 1 | 1.9 | 3.7 | 7.5 | 0.9 | 2.3 | 3.9 | 10.8 | 1.7 | 3.2 | 3.9 | 6.7 | 1.7 | 6.4 | 11.7 | 50 | 0.9 | 1.7 | 2.9 | 7.2
NEUVI | NEUVI 70 | 70 | 4.5273 | 50.172 | 2.5 | 28.4 | 45.6 | 50 | 0.5 | 1 | 5.2 | 31.4 | 1 | 10.2 | 22.9 | 50 | 0.6 | 0.8 | 1.1 | 2 | 0.5 | 1 | 5.2 | 31.4
NEUVI | NEUVI150 | 150 | 4.5273 | 50.172 | 5.6 | 28 | 52.5 | 132 | 5.7 | 54.3 | 119.1 | 166.2 | 10.2 | 31.1 | 75.4 | 175 | 15 | 73.1 | 124.7 | 175 | 5.6 | 21.9 | 33 | 91.1
NIEUW | NIEUW 36 | 36 | 3.7156 | 51.068 | 7.6 | 20 | 20 | 20 | 2.6 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 4.2 | 20 | 20 | 20 | 2.6 | 9.4 | 12.7 | 20
NIEUW | NIEUW150 | 150 | 3.7156 | 51.068 | 66.3 | 175 | 175 | 175 | 103.1 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 151.3 | 175 | 175 | 175 | 14.3 | 25.6 | 42.6 | 105.8
NINOV | NINOV 70 | 70 | 4.0085 | 50.8422 | 1.6 | 10.4 | 16.1 | 27.5 | 1.3 | 1.6 | 1.7 | 2.1 | 2.4 | 9.1 | 11.8 | 19.5 | 1.5 | 2.2 | 2.7 | 3.9 | 1.3 | 1.6 | 1.7 | 2.1
NORDL | NORDL150 | 150 | 4.2514 | 51.3698 | 8.6 | 129.6 | 175 | 175 | 100.7 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 8.6 | 121.8 | 166.5 | 175
OISQU | OISQU 70 | 70 | 4.2247 | 50.6661 | 2.9 | 9.2 | 17.6 | 30 | 3.6 | 8.5 | 11.8 | 19.3 | 14.3 | 50 | 50 | 50 | 5.2 | 9 | 14.4 | 24 | 2.4 | 8.3 | 11.8 | 19.3
OISQU | OISQU150 | 150 | 4.2247 | 50.6661 | 2.6 | 4.8 | 11.9 | 153.1 | 2.8 | 14 | 72.1 | 175 | 54.1 | 175 | 175 | 175 | 3.8 | 106 | 175 | 175 | 2.6 | 4.7 | 9.6 | 28.5
ON___ | ON___ 70 | 70 | 5.2746 | 50.1677 | 0.3 | 0.8 | 4.4 | 28.8 | 0.3 | 1.3 | 9.4 | 25 | 1 | 50 | 50 | 50 | 0.5 | 8.7 | 25.5 | 47.3 | 0.3 | 0.8 | 4.4 | 25
OPGLA | OPGLA 70 | 70 | 5.5523 | 51.0397 | 2.7 | 25.6 | 43.3 | 50 | 8.7 | 25.4 | 50 | 50 | 50 | 50 | 50 | 50 | 13.1 | 50 | 50 | 50 | 2.6 | 15.3 | 25.1 | 50
ORGEO | ORGEO 70 | 70 | 5.3029 | 49.8466 | 0.4 | 0.7 | 1.4 | 9.7 | 0.4 | 0.6 | 0.8 | 2.9 | 0.5 | 1 | 1.4 | 3.1 | 0.5 | 2.6 | 4.4 | 13.7 | 0.4 | 0.6 | 0.8 | 2.9
OS1ST | OS1ST220 | 220 | 2.8687 | 51.5823 | 107.4 | 175 | 175 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OS2ST | OS2ST220 | 220 | 2.919 | 51.5755 | 107.4 | 175 | 175 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OTTIG | OTTIG 36 | 36 | 4.5685 | 50.6619 | 0.5 | 10.2 | 15.6 | 20 | 2.4 | 16.3 | 20 | 20 | 7.5 | 20 | 20 | 20 | 4.2 | 20 | 20 | 20 | 0.5 | 4.9 | 9.3 | 19.1
OVERI | OVERI 70 | 70 | 5.3831 | 51.2149 | 4.3 | 20.7 | 27.8 | 50 | 7.9 | 46.6 | 50 | 50 | 50 | 50 | 50 | 50 | 11.9 | 50 | 50 | 50 | 3.2 | 17 | 25.4 | 42.1
OVERP | OVERP150 | 150 | 5.3937 | 51.2278 | 6.6 | 12 | 24.5 | 107.7 | 12.3 | 175 | 175 | 175 | 32.4 | 175 | 175 | 175 | 18.1 | 175 | 175 | 175 | 5.6 | 11.4 | 19.2 | 80.3
PACHE | PACHE150 | 150 | 4.3615 | 50.8499 | 7.3 | 12.3 | 14.5 | 20.4 | 31.8 | 175 | 175 | 175 | 72.9 | 175 | 175 | 175 | 44.2 | 150.7 | 175 | 175 | 7.2 | 11.8 | 13.6 | 18.3
PATHO | PATHO 36 | 36 | 3.2106 | 51.2537 | 17.8 | 20 | 20 | 20 | 0.6 | 20 | 20 | 20 | 2.7 | 20 | 20 | 20 | 0.6 | 20 | 20 | 20 | 0.6 | 20 | 20 | 20
PATUR | PATUR 70 | 70 | 3.8581 | 50.4025 | 0.8 | 2.7 | 3.7 | 6 | 0.8 | 5.5 | 7 | 9.2 | 1.4 | 22.7 | 27.9 | 38.1 | 1.2 | 3.8 | 6.8 | 11.7 | 0.8 | 2.6 | 3.7 | 5.9
PEPIN | PEPIN 70 | 70 | 5.8016 | 50.5698 | 20.1 | 28.8 | 38.1 | 50 | 7.2 | 32.4 | 50 | 50 | 9.3 | 21.5 | 50 | 50 | 25 | 50 | 50 | 50 | 4 | 19.6 | 24.4 | 31.4
PETRO | PETRO150 | 150 | 4.3724 | 51.202 | 4.3 | 41.6 | 87.6 | 175 | 9 | 25.8 | 44.7 | 175 | 21.7 | 40.1 | 51.2 | 92.3 | 15.3 | 38.9 | 70.2 | 175 | 3.9 | 13.4 | 44.7 | 127
PITEM | PITEM150 | 150 | 3.2685 | 50.9921 | 4.8 | 37.8 | 124.2 | 175 | 16.6 | 38.9 | 57.4 | 138.1 | 80.9 | 175 | 175 | 175 | 18.2 | 42.9 | 53.7 | 83.2 | 4.8 | 35.2 | 57.4 | 138.1
PLATE | PLATE150 | 150 | 4.3872 | 50.1898 | 1.8 | 9.9 | 15.2 | 29.4 | 7.1 | 22.6 | 34.4 | 69.2 | 12.7 | 40.9 | 99 | 175 | 18.7 | 66.8 | 90.2 | 145.2 | 1.8 | 9.9 | 15.2 | 29.4
PLENE | PLENE 70 | 70 | 5.8768 | 50.632 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PONDR | PONDR 70 | 70 | 5.0014 | 50.0955 | 0.4 | 2.1 | 8.7 | 29.1 | 0.4 | 4.1 | 8.8 | 30.3 | 0.7 | 7.4 | 17.3 | 30.6 | 0.5 | 0.9 | 1.8 | 25.4 | 0.4 | 1.2 | 7.3 | 26.7
PRECH | PRECH 70 | 70 | 5.8439 | 50.5994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
PTOUE | PTOUE 36 | 36 | 4.3416 | 50.8519 | 12.9 | 20 | 20 | 20 | 13.6 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 3.3 | 20 | 20 | 20
QDEME | QDEME 36 | 36 | 4.3186 | 50.8401 | 0.4 | 20 | 20 | 20 | 5.9 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0.4 | 20 | 20 | 20
QUEVA | QUEVA 70 | 70 | 3.6649 | 50.5145 | 1.5 | 3 | 4.8 | 7.2 | 0.8 | 6.5 | 7.9 | 10.5 | 1.4 | 26.8 | 34.7 | 48 | 1.2 | 6 | 9.3 | 15.9 | 0.8 | 2.9 | 4.8 | 7.2
RHODE | RHODE150 | 150 | 4.3553 | 50.7487 | 4 | 12.1 | 50.9 | 175 | 4.8 | 16.9 | 26.3 | 68.3 | 11.2 | 29 | 35.2 | 56.2 | 5.3 | 11.8 | 29.5 | 123.9 | 4 | 10.9 | 26.3 | 68.3
RIJKE | RIJKE150 | 150 | 4.7453 | 51.3318 | 4.3 | 95.1 | 175 | 175 | 4.1 | 8.7 | 14.3 | 46.6 | 8.2 | 15.5 | 19.9 | 36.4 | 5.6 | 17.2 | 35.6 | 98.7 | 4.1 | 8.7 | 14.3 | 46.6
RIMIE | RIMIE 70 | 70 | 5.471 | 50.5404 | 4.6 | 24 | 43 | 50 | 5.1 | 10 | 13.9 | 25.9 | 9.3 | 31 | 45.2 | 50 | 7.9 | 22.3 | 33.2 | 50 | 5.1 | 10 | 13.9 | 25.9
RIMIE | RIMIE220 | 220 | 5.471 | 50.5404 | 12.1 | 33 | 50.3 | 122.4 | 18.8 | 38.4 | 78.5 | 175 | 48.9 | 175 | 175 | 175 | 28.6 | 175 | 175 | 175 | 12 | 23 | 27.7 | 39.7
RIMIE | RIMIE380 | 380 | 5.471 | 50.5404 | 36.3 | 67 | 130.8 | 300 | 25.5 | 225.8 | 300 | 300 | 225.2 | 300 | 300 | 300 | 27.2 | 170.2 | 300 | 300 | 25.5 | 60.7 | 118 | 300
RINGV | RINGV150 | 150 | 3.7272 | 51.1067 | 7.6 | 175 | 175 | 175 | 77.6 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 119.7 | 175 | 175 | 175 | 5.9 | 9.1 | 11.8 | 25.2
RODEN | RODEN150 | 150 | 3.7753 | 51.1328 | 34.9 | 300 | 300 | 300 | 100.8 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 119.7 | 256.3 | 300 | 300 | 32.5 | 43.9 | 58 | 128.7
ROEVG | ROEVG 36 | 36 | 3.748 | 51.1084 | 7.6 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 5.9 | 9.4 | 12.4 | 20
ROMSE | ROMSE220 | 220 | 5.6606 | 50.6138 | 14.7 | 27.3 | 42.5 | 87.4 | 3.6 | 25 | 71.9 | 175 | 37.3 | 175 | 175 | 175 | 9.9 | 175 | 175 | 175 | 3.6 | 19.3 | 23 | 33.3
ROSIE | ROSIE 36 | 36 | 4.5304 | 50.7401 | 0.8 | 20 | 20 | 20 | 1 | 20 | 20 | 20 | 7.5 | 20 | 20 | 20 | 1.3 | 20 | 20 | 20 | 0.8 | 11.2 | 20 | 20
RUIEN | RUIEN 70 | 70 | 3.4874 | 50.7818 | 4.1 | 28.3 | 60 | 60 | 24.3 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 4.1 | 21.3 | 30 | 60
RUIEN | RUIEN150 | 150 | 3.4874 | 50.7818 | 14.3 | 27.8 | 113.2 | 175 | 23.8 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 79.5 | 175 | 175 | 175 | 14.3 | 25.7 | 41.7 | 116.2
SAIVE | SAIVE 70 | 70 | 5.2361 | 50.6678 | 1.4 | 4 | 11.1 | 43.4 | 2.3 | 28.4 | 46.3 | 50 | 3.9 | 50 | 50 | 50 | 3.3 | 18.5 | 36.7 | 50 | 1.3 | 4 | 13.1 | 31.3
SAMAN | SAMAN 36 | 36 | 3.7555 | 51.0513 | 2.3 | 20 | 20 | 20 | 1.1 | 20 | 20 | 20 | 14.6 | 20 | 20 | 20 | 3 | 20 | 20 | 20 | 1.1 | 4.4 | 8.3 | 16.6
SART | SART 220 | 220 | 5.5598 | 50.59 | 8.8 | 26.7 | 36.7 | 74.9 | 7.3 | 27.6 | 64.6 | 175 | 132.9 | 175 | 175 | 175 | 20.1 | 175 | 175 | 175 | 6.9 | 19.9 | 23.6 | 32.6
SART | SART 70 | 70 | 5.5598 | 50.59 | 2.8 | 28.8 | 38.9 | 50 | 7 | 14.3 | 25 | 50 | 13.7 | 50 | 50 | 50 | 10.3 | 50 | 50 | 50 | 6.8 | 14.3 | 25 | 35.5
SCARB | SCARB 36 | 36 | 4.3799 | 50.8818 | 8.7 | 12.3 | 14.7 | 20.7 | 31.8 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 44.2 | 60 | 60 | 60 | 8.7 | 11.9 | 13.6 | 18.4
SCARB | SCARB150 | 150 | 4.3799 | 50.8818 | 8.7 | 12.3 | 14.7 | 20.7 | 31.8 | 175 | 175 | 175 | 72.9 | 175 | 175 | 175 | 44.2 | 150.7 | 175 | 175 | 8.7 | 11.9 | 13.6 | 18.4
SCHED | SCHED 70 | 70 | 4.3393 | 51.1238 | 5.6 | 12.9 | 16.5 | 34.4 | 5.7 | 24.3 | 29.8 | 43.3 | 21.9 | 49.7 | 60 | 60 | 5.4 | 60 | 60 | 60 | 5.6 | 11.8 | 15.1 | 25.6
SCHEL | SCHEL 70 | 70 | 4.3124 | 51.1233 | 5.6 | 12.7 | 16.4 | 34.3 | 5.4 | 24.8 | 30.4 | 46.4 | 24.1 | 50 | 50 | 50 | 5.1 | 50 | 50 | 50 | 5.4 | 11.7 | 15 | 25.2
SCHEL | SCHEL150 | 150 | 4.3124 | 51.1233 | 6.3 | 12.3 | 15.7 | 32.6 | 16.1 | 21.4 | 26.1 | 41.7 | 44.2 | 147.3 | 175 | 175 | 18.8 | 39.8 | 62.7 | 123.2 | 6.3 | 11.5 | 14.4 | 24.1
SDALE | SDALE150 | 150 | 3.3835 | 50.8917 | 4.7 | 32.3 | 111.9 | 175 | 48.8 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 62.9 | 170.6 | 175 | 175 | 4.1 | 6.9 | 10.5 | 32.9
SDEWE | SDEWE 36 | 36 | 3.6777 | 51.0187 | 0.5 | 17.3 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0.5 | 4.8 | 13.5 | 20
SEILL | SEILL 70 | 70 | 5.1063 | 50.5019 | 1.3 | 2.5 | 5.7 | 25.2 | 0.9 | 4.3 | 25.9 | 50 | 1.5 | 6 | 26.8 | 50 | 1.1 | 3.4 | 5.8 | 25.4 | 0.9 | 1.9 | 2.9 | 6.2
SENEF | SENEF 70 | 70 | 4.252 | 50.5267 | 1.9 | 11.6 | 21.3 | 50 | 5.8 | 12 | 17.2 | 33.9 | 17.5 | 50 | 50 | 50 | 8.1 | 14 | 21.5 | 50 | 1.1 | 11.2 | 17.2 | 33.9
SERAI | SERAI220 | 220 | 5.5229 | 50.6141 | 6.6 | 26.3 | 36 | 71.4 | 11 | 32.3 | 74.1 | 175 | 144.1 | 175 | 175 | 175 | 27.1 | 175 | 175 | 175 | 6.6 | 19.7 | 23.4 | 31.7
SIDAL | SIDAL150 | 150 | 4.4764 | 51.0823 | 3.5 | 8 | 13.1 | 21.3 | 9.3 | 26.2 | 31.5 | 42.3 | 27.4 | 52.3 | 66.2 | 99.4 | 10.7 | 34.9 | 62.6 | 100.4 | 3.3 | 5.7 | 10.8 | 17.2
SJOB | SJOB 70 | 70 | 4.5721 | 51.3023 | 6.4 | 50 | 50 | 50 | 7.5 | 34.4 | 47.1 | 50 | 17.5 | 50 | 50 | 50 | 12 | 37.1 | 50 | 50 | 6.1 | 20.2 | 47.1 | 50
SLAAN | SLAAN 36 | 36 | 4.3432 | 51.2506 | 4.2 | 4.9 | 5.2 | 6 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 4.2 | 4.9 | 5.2 | 5.9
SLAAN | SLAAN150 | 150 | 4.3432 | 51.2506 | 4.2 | 4.9 | 5.2 | 6 | 101.4 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 142.3 | 175 | 175 | 175 | 4.2 | 4.9 | 5.2 | 5.9
SLYKE | SLYKE 36 | 36 | 2.9529 | 51.2234 | 9.7 | 60 | 60 | 60 | 7.2 | 60 | 60 | 60 | 11.6 | 60 | 60 | 60 | 32.9 | 60 | 60 | 60 | 1.1 | 1.4 | 1.6 | 2
SLYKE | SLYKE150 | 150 | 2.9529 | 51.2234 | 23.4 | 94.4 | 175 | 175 | 7.2 | 175 | 175 | 175 | 11.6 | 175 | 175 | 175 | 32.9 | 175 | 175 | 175 | 6.4 | 46.7 | 146.1 | 175
SMARD | SMARD220 | 220 | 5.5143 | 49.5513 | 18.4 | 31.6 | 47.4 | 90.6 | 23.1 | 54.6 | 122.8 | 175 | 29.7 | 97.5 | 159.2 | 175 | 37.2 | 101.9 | 175 | 175 | 18.4 | 31.4 | 46.1 | 86.1
SOLRE | SOLRE 70 | 70 | 4.2536 | 50.2127 | 2.4 | 24.8 | 31.7 | 50 | 0.4 | 0.7 | 1.2 | 9.8 | 0.8 | 10.2 | 23 | 49.6 | 0.5 | 0.7 | 0.8 | 1.3 | 0.4 | 0.7 | 1.2 | 9.8
STALE | STALE150 | 150 | 5.5117 | 50.9924 | 7.8 | 28.5 | 35.9 | 73 | 50.6 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 82.1 | 175 | 175 | 175 | 7.8 | 21.8 | 34.2 | 69
STBAV | STBAV150 | 150 | 3.3973 | 50.9105 | 10 | 31.5 | 109.3 | 175 | 55 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 64.6 | 172.9 | 175 | 175 | 4.3 | 7.4 | 11.2 | 35.1
STEMB | STEMB 70 | 70 | 5.8893 | 50.5979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
STENE | STENE 36 | 36 | 2.945 | 51.2145 | 6.7 | 20 | 20 | 20 | 7.2 | 20 | 20 | 20 | 11.6 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0.2 | 1.4 | 1.5 | 2
STEVN | STEVN220 | 220 | 3.1848 | 51.3133 | 107.4 | 175 | 175 | 175 | 46.8 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 55.6 | 175 | 175 | 175 | 46.8 | 175 | 175 | 175
STEVN | STEVN380 | 380 | 3.1848 | 51.3133 | 107.4 | 300 | 300 | 300 | 142.5 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 163.2 | 300 | 300 | 300 | 107.4 | 300 | 300 | 300
STHUI | STHUI 70 | 70 | 5.4786 | 51.2374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
STRUI | STRUI 70 | 70 | 5.1979 | 50.8105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
SVITH | SVITH 70 | 70 | 6.1356 | 50.2804 | 1.3 | 38 | 48.4 | 50 | 0.4 | 0.7 | 1.4 | 14.7 | 0.7 | 6.6 | 17 | 35.3 | 0.5 | 0.7 | 0.9 | 1.6 | 0.4 | 0.7 | 1.4 | 14.7
TABAK | TABAK 70 | 70 | 4.4098 | 51.2139 | 5.8 | 35.5 | 43 | 50 | 8.1 | 22.7 | 39 | 50 | 19.4 | 35.8 | 45.7 | 50 | 13.3 | 34.8 | 50 | 50 | 5.4 | 22.7 | 39 | 49.9
GEZEL | GEZEL220 | 220 | 3.2012 | 51.2639 | 105.5 | 175 | 175 | 175 | 138.8 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 158.9 | 175 | 175 | 175 | 105.5 | 175 | 175 | 175
TERGN | TERGN150 | 150 | 4.5679 | 50.4368 | 4.5 | 18.8 | 28.8 | 54.6 | 5.3 | 40.2 | 79.5 | 203.3 | 22.3 | 294.4 | 300 | 300 | 13.4 | 90.6 | 184.1 | 300 | 4.5 | 11.7 | 22.1 | 38.3
TERGN | TERGN380 | 380 | 4.5679 | 50.4368 | 18.8 | 69.8 | 178.5 | 300 | 18.4 | 30.4 | 54.5 | 300 | 38.2 | 254.8 | 300 | 300 | 64 | 300 | 300 | 300 | 18.4 | 30.4 | 54.5 | 300
TERTR | TERTR 30 | 30 | 3.7964 | 50.4801 | 5 | 20 | 20 | 20 | 8 | 20 | 20 | 20 | 10.3 | 19.3 | 20 | 20 | 17.5 | 20 | 20 | 20 | 5 | 20 | 20 | 20
THYCH | THYCH 70 | 70 | 4.4418 | 50.2801 | 3.6 | 11.5 | 31.9 | 50 | 0.7 | 7.4 | 18.1 | 49.7 | 1.2 | 25.7 | 41.2 | 50 | 0.8 | 1.5 | 2.8 | 18.9 | 0.7 | 7.4 | 18.1 | 46.4
TIELT | TIELT150 | 150 | 3.34 | 50.9793 | 4.8 | 37.1 | 115.5 | 154.9 | 16.6 | 30.9 | 46.4 | 114.1 | 80.9 | 175 | 175 | 175 | 18.2 | 37.1 | 47.1 | 74.2 | 4.8 | 30.9 | 46.4 | 114.1
TIENE | TIENE150 | 150 | 4.9264 | 50.8148 | 4.8 | 38.2 | 50.2 | 94.6 | 92.3 | 175 | 175 | 175 | 117.4 | 175 | 175 | 175 | 138.1 | 175 | 175 | 175 | 4.7 | 23.7 | 39.9 | 60.7
TIP | TIP 70 | 70 | 5.1615 | 51.0628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TISLT | TISLT 70 | 70 | 4.3564 | 51.025 | 0.8 | 2.4 | 12.4 | 19.3 | 10.9 | 50 | 50 | 50 | 48.5 | 50 | 50 | 50 | 21.3 | 50 | 50 | 50 | 0.8 | 1.4 | 2.7 | 8.8
TONGE | TONGE 70 | 70 | 5.4351 | 50.7751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TORHO | TORHO 36 | 36 | 3.1059 | 51.0758 | 0.4 | 17.6 | 20 | 20 | 0 | 20 | 20 | 20 | 0 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0 | 15.3 | 18.9 | 20
TOURN | TOURN 70 | 70 | 3.3803 | 50.6224 | 3.6 | 27.5 | 50 | 50 | 25 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47.1 | 50 | 50 | 50 | 3.1 | 23.2 | 50 | 50
TRIVI | TRIVI150 | 150 | 4.1378 | 50.4535 | 10.1 | 21.7 | 30.7 | 52.9 | 19 | 49.8 | 69.5 | 108.7 | 60.3 | 175 | 175 | 175 | 32.6 | 67.7 | 143.7 | 175 | 9.5 | 20.8 | 28 | 45.3
TURNH | TURNH 70 | 70 | 4.9335 | 51.312 | 1 | 2.8 | 26.6 | 50 | 1.5 | 7.8 | 13.1 | 37.5 | 2.9 | 18 | 22.6 | 39.4 | 2.5 | 19.1 | 35 | 50 | 1 | 2.8 | 13.1 | 37.5
TURON | TURON 70 | 70 | 5.8199 | 50.5135 | 20.1 | 28.8 | 37.7 | 48.7 | 5.5 | 40.4 | 50 | 50 | 9.3 | 21.5 | 50 | 50 | 25 | 50 | 50 | 50 | 4 | 19.7 | 24.4 | 31.3
VANYK | VANYK380 | 380 | 5.7739 | 51.1213 | 99.9 | 300 | 300 | 300 | 288 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 99.9 | 300 | 300 | 300
VERBR | VERBR150 | 150 | 4.4224 | 50.9409 | 9.5 | 12.4 | 14.3 | 19.1 | 31.8 | 289.8 | 300 | 300 | 72.9 | 300 | 300 | 300 | 44.2 | 150.7 | 300 | 300 | 9.5 | 11.8 | 13.2 | 16.9
VHAIN | VHAIN150 | 150 | 4.0723 | 50.469 | 12.8 | 33.9 | 43 | 74.5 | 20.2 | 41.1 | 51 | 67.3 | 52.2 | 158.7 | 175 | 175 | 26.8 | 68.2 | 85.4 | 120.4 | 12.9 | 23 | 31.7 | 52.3
VILLE | VILLE 70 | 70 | 5.6626 | 49.9759 | 1.4 | 5 | 7.5 | 20.2 | 1.3 | 4.6 | 7.2 | 28.1 | 2.2 | 50.5 | 60 | 60 | 1.5 | 6.1 | 25.5 | 60 | 1.3 | 4.6 | 7.2 | 23.7
VILLE | VILLE220 | 220 | 5.6626 | 49.9759 | 7.5 | 37.8 | 50.2 | 83.5 | 4.6 | 20.2 | 60.9 | 141.9 | 14.8 | 175 | 175 | 175 | 6.8 | 65.6 | 155.4 | 175 | 4.6 | 20.2 | 49.5 | 81.4
VISEM | VISEM 70 | 70 | 5.5607 | 49.6963 | 0.9 | 2.8 | 3.6 | 7.1 | 1 | 3.3 | 4.9 | 14.9 | 2.7 | 5.1 | 6.3 | 10.5 | 2.7 | 10 | 20.1 | 50 | 0.9 | 2.7 | 4.9 | 14.9
VTAIR | VTAIR 36 | 36 | 4.3805 | 50.8635 | 8.7 | 12.3 | 14.5 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 8.7 | 11.8 | 13.6 | 18.3
WAARS | WAARS 36 | 36 | 3.6171 | 51.1534 | 1.6 | 12.1 | 13.6 | 16 | 0.6 | 19.8 | 20 | 20 | 1 | 20 | 20 | 20 | 16.1 | 20 | 20 | 20 | 0.6 | 10.3 | 12.5 | 15
WARNA | WARNA 70 | 70 | 4.84 | 50.3211 | 3.9 | 8.2 | 25.8 | 50 | 0.4 | 0.4 | 0.5 | 0.6 | 0.5 | 1.2 | 1.6 | 2.4 | 0.4 | 0.6 | 0.6 | 0.9 | 0.4 | 0.4 | 0.5 | 0.6
WEZEM | WEZEM 36 | 36 | 4.4856 | 50.8552 | 4.9 | 12.1 | 14.1 | 19.4 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 0.7 | 11.2 | 12.7 | 16.2
WICHE | WICHE 36 | 36 | 3.9913 | 51.0015 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WIJGM | WIJGM150 | 150 | 4.6922 | 50.939 | 5.2 | 10.3 | 12.6 | 15.6 | 22.4 | 161.4 | 175 | 175 | 59.9 | 175 | 175 | 175 | 38.8 | 132.3 | 175 | 175 | 5 | 9.7 | 11.3 | 14.3
WILRI | WILRI 70 | 70 | 4.3761 | 51.1705 | 6.4 | 10.4 | 12.5 | 18.7 | 5.6 | 35.5 | 50 | 50 | 23 | 50 | 50 | 50 | 5.3 | 50 | 50 | 50 | 5.6 | 10.2 | 11.9 | 16.6
WILSE | WILSE 70 | 70 | 4.7081 | 50.9025 | 3.5 | 8.7 | 11.7 | 17.9 | 34.5 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 3.5 | 7.2 | 10.5 | 15.4
WILSE | WILSE150 | 150 | 4.7081 | 50.9025 | 2.8 | 8 | 14.4 | 21 | 34.6 | 175 | 175 | 175 | 129.3 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 2.8 | 5.8 | 10.6 | 16.5
WIRTZ | WIRTZ 36 | 36 | 4.3763 | 50.8394 | 4.3 | 20 | 20 | 20 | 5.8 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 4 | 20 | 20 | 20
WOLUW | WOLUW 36 | 36 | 4.4603 | 50.8502 | 4.9 | 12.2 | 14.5 | 20.3 | 31.8 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 44.2 | 60 | 60 | 60 | 1 | 11.2 | 13.1 | 17.4
WOLUW | WOLUW150 | 150 | 4.4603 | 50.8502 | 5.4 | 12.2 | 14.5 | 20.3 | 31.8 | 175 | 175 | 175 | 72.9 | 175 | 175 | 175 | 44.2 | 150.7 | 175 | 175 | 5.4 | 11 | 13 | 17.4
WORTG | WORTG 70 | 70 | 3.4865 | 50.8628 | 1.5 | 24.2 | 45.1 | 50 | 1.5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 46.6 | 50 | 50 | 50 | 1.4 | 3.3 | 8.9 | 24
WORTG | WORTG150 | 150 | 3.4865 | 50.8628 | 15.7 | 28.5 | 101.6 | 175 | 57.1 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 99.2 | 175 | 175 | 175 | 4.6 | 12.4 | 18.7 | 58.7
WVLGM | WVLGM150 | 150 | 3.147 | 50.7995 | 14.6 | 34.5 | 76.4 | 108 | 48.1 | 175 | 175 | 175 | 164.8 | 175 | 175 | 175 | 99.8 | 175 | 175 | 175 | 3.1 | 31 | 53.2 | 78.7
ZANDV | ZANDV150 | 150 | 4.2481 | 51.3695 | 7.8 | 186.5 | 234.5 | 298.8 | 62.6 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 183.6 | 300 | 300 | 300 | 7.8 | 186.5 | 234.5 | 298.8
ZANDV | ZANDV380 | 380 | 4.2481 | 51.3695 | 94.7 | 300 | 300 | 300 | 237.3 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 92.8 | 300 | 300 | 300
ZARCP | ZARCP 36 | 36 | 4.4821 | 50.8666 | 4.9 | 12.1 | 14.2 | 19.8 | 1.9 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 2.6 | 20 | 20 | 20 | 1.9 | 11.2 | 13 | 16.8
ZARCP | ZARCP150 | 150 | 4.4821 | 50.8666 | 4.8 | 12.1 | 14.2 | 19.8 | 31.8 | 175 | 175 | 175 | 72.9 | 175 | 175 | 175 | 44.2 | 150.9 | 175 | 175 | 4.8 | 11.1 | 13 | 16.8
ZAVEN | ZAVEN 36 | 36 | 4.4776 | 50.8861 | 4.9 | 12.2 | 14.4 | 20 | 1.9 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 2.7 | 20 | 20 | 20 | 1.9 | 11.2 | 13.1 | 17.1
ZBZSL | ZBZSL 36 | 36 | 3.2186 | 51.3348 | 9.2 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 5 | 37.8 | 51.4 | 60
ZBZSL | ZBZSL150 | 150 | 3.2186 | 51.3348 | 9.2 | 116.8 | 175 | 175 | 141.3 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 161.7 | 175 | 175 | 175 | 5 | 43.9 | 125.9 | 175
ZECHP | ZECHP 36 | 36 | 3.2248 | 51.3493 | 9.2 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 5 | 20 | 20 | 20
ZEDEL | ZEDEL 36 | 36 | 3.1558 | 51.1309 | 17.8 | 60 | 60 | 60 | 0 | 60 | 60 | 60 | 0 | 60 | 60 | 60 | 30.7 | 60 | 60 | 60 | 0 | 60 | 60 | 60
ZEEBR | ZEEBR 36 | 36 | 3.1926 | 51.3186 | 9.2 | 58.4 | 60 | 60 | 8.2 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 11.4 | 60 | 60 | 60 | 1.1 | 2.1 | 5.1 | 13.5
ZEEBR | ZEEBR150 | 150 | 3.1926 | 51.3186 | 9.2 | 103.6 | 175 | 175 | 8.2 | 175 | 175 | 175 | 79.7 | 175 | 175 | 175 | 11.4 | 175 | 175 | 175 | 8.2 | 105.1 | 175 | 175
ZELEI | ZELEI 36 | 36 | 4.0505 | 51.078 | 1.1 | 9.4 | 60 | 60 | 11.1 | 13.3 | 14.6 | 18.1 | 20.6 | 60 | 60 | 60 | 12.7 | 19.2 | 23.5 | 32.8 | 1.1 | 3.1 | 14.6 | 18.1
ZONHO | ZONHO 70 | 70 | 5.3479 | 50.9908 | 3.5 | 16.3 | 23.7 | 35 | 6 | 17.7 | 50 | 50 | 50 | 50 | 50 | 50 | 9.1 | 50 | 50 | 50 | 1.3 | 17.7 | 32.9 | 50
ZOTGM | ZOTGM 70 | 70 | 3.8163 | 50.8795 | 1.9 | 15.7 | 21.5 | 34.4 | 1.3 | 1.8 | 2.5 | 6.4 | 2.4 | 15.2 | 29.1 | 50 | 1.7 | 3.2 | 5.5 | 12 | 1.2 | 1.8 | 2.4 | 3
ZUDOK | ZUDOK 36 | 36 | 3.2376 | 51.3066 | 9.2 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 1.1 | 2.1 | 5.1 | 13.9
ZUREN | ZUREN 70 | 70 | 4.4364 | 51.2046 | 5.7 | 35.6 | 43.3 | 50 | 8.1 | 24.1 | 48.3 | 50 | 19.5 | 45.1 | 50 | 50 | 13.4 | 41.2 | 50 | 50 | 5.4 | 24.1 | 40.1 | 50
ZUREN | ZUREN150 | 150 | 4.4364 | 51.2046 | 5 | 44.3 | 90.3 | 175 | 9 | 27.7 | 55.5 | 175 | 22.4 | 51.8 | 75.8 | 132.1 | 15.3 | 47.2 | 97.6 | 175 | 3.9 | 13.4 | 55.5 | 135
ZWIJN | ZWIJN 36 | 36 | 4.3284 | 51.2313 | 4.2 | 4.9 | 5.2 | 6 | 4.5 | 6.9 | 9.2 | 25.2 | 10.7 | 60 | 60 | 60 | 8.3 | 60 | 60 | 60 | 4.2 | 4.9 | 5.2 | 5.9
ZWIJN | ZWIJN150 | 150 | 4.3284 | 51.2313 | 4.2 | 4.9 | 5.2 | 6 | 4.5 | 6.9 | 9.2 | 25.2 | 10.7 | 126.8 | 175 | 175 | 8.3 | 80 | 175 | 175 | 4.2 | 4.9 | 5.2 | 5.9